## DATA (hidden)
ID#: | A211655
Province: | Badghis
District : | QIN
Village : | Arbab Mohammad
Project Purpose: Construction of Solar Powered Water Supply Network
USD Rate | 0 | 0
Item | Quantity | Unit | Total
Cement | 1 | ton | 0
Reinforcing Bar | 1 | ton | 0
Tap Stand No | 8
L pipe
Total Length of Pipe | 1771
Targeted papulation 150 Family, 1050 People
150

## ToR for Morichaq SPWS Network
| QIN Zonal Office | Province: Badghis
| Project: DAWAM/FCDO | District: Bala Murghab
| Project #:A221873 | Village: Morichaq
| Date: Feb 01, 2024 | Type:SPWS Network
NO | ITEMS موضوعات | UNIT واحد | Work quantity and cost estimated برآورد احجام کاری
|  |  | QUANTITY مقدار | Unit Cost (Af) قیمت فی واحد | Total cost(Afs) قیمت مجموعی
1 | Site Preparation: to clean site from all existent materials. | M2 | 400
2 | Excavation: In ordinary soil-type three, excavation will be take place for different types of structure as per drawing and spesification. | M3 | 256
3 | PCC (M-150, 1:2:4): The PCC work is for plecement under the collecting stand according to the drawing considering the shuttering needs, using cement sand mortar base on given specifications. • Curing should be done for minimum 7 days. | M3 | 3.042
4 | Painting: The work should be get done in proper way as per the drawing and specification any input of the site engineer. | M2 | 56
5 | Back filling: Back filling from excatated materials | M3 | 256
Piping and fitting work of Network
6 | Pipe 20mm HDPЕ 100: Pipe 20mm OD, HDPЕ 100, РN-16, Thickness 2.3 mm & Weight 0.133kg/m | m | 800
7 | Pipe Fittings | lot | 1
8 | Metering System: House connection from main pipe to inside houses, public buildings (school, mosque and clinic) with its all accessories including 1/2" Saddle clamp, Elbow, Female threaded adapter, (MTA), Gate valve, Water meter, Non return valve, Water tap, Socket and 3m 1/2"m GI pipe for every meter. | lot | 250
Solar System
9 | Solar panels: Solar panels 270 watt, standard : Range of ambient temperature: 233 .. 358 K Electrical data: Maximum power point voltage: 30.9 V. to 31.2 V. Open circuit voltage: 37,7 V to 45.8 Max power point current: 8.42 A Module shortcut current: 8.89 A Maximum power output: 260 W to 270 W. Solar module type: POLYCRYSTALLINE or MONOCRYSTALLINE CE certificate for monocrystalline and monocrystalline, ISO 9001:2007 Certificate, DIN EN certificate, Efficiency for Monocrystalline 18%-20%, Efficiency for Polycrystalline 15%-18%, Performance to 10 years (min 90% power output), Performance to 25 years (min 80% power output), Visible label on solar panel with technical specification and accepted by MRRD. | No | 3
10 | Submersible Water Pump: 7.5kW; 10HP 10.08 m3/h at head (70-230) m with min 2 years warranty - prefered brands are: Aquastrong, DK Pump, Envision, Grundfos, Grundfos- Germany, Leo/Franklin, Lorentz, Germany, Lorentz/Vansan Maxisu, Pedrollo- Italy, Shakti, Solartech, Frog | No | 1
11 | electrical solar cable 2*4mm2 | m | 30
Drilling of Well
12 | Well drilling with percussion machine with 16" dia depend on soil texture | m | 10
13 | Gravel based on soil texure, Gravel sized from 3mm to 6 mm according to the soil texture, as per advise of WVA WASH Engineer | m | 3.43
14 | Pump Test for detemination of Hydrogeological parameters | Hour | 8
15 | Steel Plate for Well Cover | No | 1
16 | Supplying and installation of all required fittings for well | Lot | 1
17 | Supplying and installation of mettalic sign board | Lot | 1
Total Cost
This BoQ contains required in the Offer documents and shall be signed by a duly authorized person. Any addition, deletion or alteration in the BoQ may result in rejection of the Offer.Please have a Site visit before submit your offer and also attache the site visit picture with your bid documents
The works actually executed shall be measured, contractor shall visit the site of the works and obtain all information that may be necessary for completing their offer as under the provision of this contract no claim for additional work is accepted once the contract is signed.
Mobilization, Demobilization, Access road to construction site or other temporary works required for the execution of the items listed above, plus site restoration will be the responsibility of the contractor. Hence all the unit prices above are assumed to cover all activities associated with the works mentioned, and the total contract cost quoted is all inclusive to complete the total works.
Work Completion Certificate will provide after the measurement take place by WV team. The network scheme (length of the pipes) may change in field due to the commuity members request so the pipes will measure base on actule work completed in field with consideration of the quality of the work then the work completion certification will provide.