## Cover Sheet
Project Name: | Water Supply (Bore Wells) for 9 Family Health Houses in Various Districts of Faryab and Balkh
Project type: | Water Supply for Family Health Houses including: Geophysical analysis (Hydro-geological survey), Construction and Drilling of Water Well with installation of the solar pump and solar panels and connected to the existing water tank, and construction of well chamber.
Project code: | Fariab - 04, Balkh - 05
Province: | Faryab and Balkh
District | 1. Dowlat Abad 2. Pashton kot 3. Qaisar 4. Almar 5. Belcheragh 6. Gurziwan 7. Shor Tepa
Village: | 1. Popalzai, Jangal 2. Atakhan Khaja 3. As-hab Kahf 4. Khaja Asplan 5. Qara kol 6. Kata Tash 7. Ghulbian 8. Islam Chongar 9. Sar-e-Pata village
CDC Name; | 1. Popalzai, Jangal 2. Atakhan Khaja 3. As-hab Kahf 4. Khaja Asplan 5. Qara kol 6. Kata Tash 7. Ghulbian 8. Islam Chongar 9. Sar-e-Pata village
Expected Project Start date:
Expected Project completion date:
Project Duration

## BoQ
Bill of Quantity (BoQ)
Province: Faryab and Balkh
Project: Water Supply (Bore Wells) for 9 Family Health Houses in Various Districts of Faryab and Balkh
Project Code: Fariab - 04, Balkh - 05 - RFQ Ref. No. AF10/RFQ/24/0302
Date: | 2024-07-22 | [12 empty] | Annex 3
Preambles and General Requirements/Guidelines
Attention to Tenderer Responsibilities: The tenderer is reminded to thoroughly review the Bill of Quantities (BOQ), Drawings, Conditions of Contract, Specifications, and any related documents. It is incumbent upon the tenderer to ensure that their pricing encompasses compliance with all contract conditions, whether explicitly referenced in the BOQ or not. Contract Basis and Site Visit Advice: The contract is established on the foundation of contract drawings, BOQ, and specifications. Tenderers are strongly advised to visit the proposed work site to familiarize themselves with access conditions, external working space, storage area availability, etc. Handling Discrepancies and Corrections: In case of discrepancies, omissions, or corrections in the BOQ, drawings, and technical specifications, the tenderer must document identified variations separately and submit relevant BOQ adjustments to IOM before tender submission. Failure to do so may preclude cost/price corrections post-contract agreement. Inclusive Rate Requirements: Rates must encompass providing material samples, conducting tests, and furnishing test results. Additionally, rates should cover specifications, model numbers, maintenance manuals, makes, technical information, and catalog literature as requested by IOM engineers, without extra payment allowances. Comprehensive Construction Implementation: Rates should encompass all construction implementation necessities, including equipment, tools, supervision, QC/QA mechanisms, logistics, etc.
Pre-Construction Checks: Prior to commencing work, the Contractor must verify all dimensions specified in the BOQ, drawings, or specifications at the site. Any discrepancies should be promptly communicated to the Engineer for appropriate guidance. Design and Execution Consistency: Contractors must ensure consistency between design plans and BOQ execution. In cases of discrepancies between BOQ and technical drawings, the BOQ takes precedence. Contractual Obligations: All BOQ tasks entail supplying manpower, machinery, equipment, transportation, local permits, and meeting contractual requirements, subject to national technical standards and under IOM Project Engineer supervision. Debris Removal and Material Sourcing: Contractors are responsible for removing and transporting debris to designated disposal areas. Local material sourcing is encouraged, with vendors potentially required to provide test certificates and bear testing costs. Community Engagement and Labor Sourcing: Encouragement is given for sourcing labor from within the settlement location and coordinating with community leaders during construction endeavors.
S/N | Description | Unit | Unit Rate USD | Faryab | [6 empty] | Balkh |  | Total Quantity | Total Price (USD) | Remarks
|  |  |  | Dowlat Abad District | Pashton kot District | Qaisar District |  | Almar District | Belcheragh District | Gurziwan District | Shor Tepa District
|  |  |  | Popalzai, Jangal village | Atakhan Khaja village | As-hab Kahf village | Khaja Asplan village | Qara kol village | Kata Tash village | Ghulbian village | Islam Chongar village | Sar-e-Pata village
Quantity
1 | Water Well
1.1 | GROUNDWATER INVESTIGATION Borehole locations shall be identified in agreement with the local communities and in consultation with the IOM Project Engineer. Borehole locations shall be identified in agreement with the local communities and in consultation with the IOM Project Engineer. Prior to drilling and installation works commencing, the Contractor must perform a geophysical survey and analysis (hydrogeological survey) in the IOM project locations using geoelectrical techniques. The purpose of the surveys will be to identify optimal drilling position at each location, as well as two back up drilling positions. The hydrogeologist shall recommend three suitable sites with the view that the proposed drilling will take place in the location where the demanded yield shall be attained as described in the TOR or minimum of 4 m3/hr. The results of these geophysical surveys will be compiled into a ‘Geophysical Survey Report’ to be submitted to the IOM Technical Engineer prior to drill operations commencing. This report will contain all results and locations of all geophysical profiles undertaken, and coordinates for the optimal and back up drilling positions. The IOM Technical Engineer will review this document and agree the proposed drilling positions are suitable prior to commencing however full responsibility will be carried by contractor where any miss-drilling will not be paid to the contractor. | Job | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 8 | 0
1.2 | Drilling of 10 Inches (25.4 Cm) diameter water well according to the EPA norms, with rotary machinery, with all necessary works,Minimum yield 0.85 l/sec supply and installation of all needed machinery & equipment for drilling and development along with other needed miscellaneous materials, as per design, drawing and specifications. * Length of casing and screen/filter to be determined once the water well borehole drilling records and log book are obtained and studied. | m | 0 | 120 | 145 | 80 | 80 | 135 | 120 | 60 | 110 | 110 | 960 | 0
1.3 | Supply and Installation of PVC casings pipe Class E, diameter 6 inches (BSI - BS 3505), and as per technical specification, and drawings. | m | 0 | 45 | 55 | 35 | 35 | 50 | 45 | 25 | 45 | 45 | 380 | 0
1.4 | Supply and Installation of PVC Filter/screen pipe class -E, dia. 6 inches (BSI - BS 3505), and as per technical specfication, and drawings. | m | 0 | 75 | 90 | 45 | 45 | 85 | 75 | 35 | 65 | 65 | 580 | 0
1.5 | Gravel Packing The Contractor will supply and install a filter gravel pack which are washed and well-rounded, with uniform grading from riverbeds, consisting of particles with diameters ranging from 1-5mm. The gravel pack should be composed of at least 95% siliceous material and must not contain clay, shale, silt, fines, excessive calcareous material, or crushed rock. Before delivery, the IOM Field Engineer will inspect a sample of the gravel pack for validation. The required volume of the filter pack must be calculated, taking into account the length of the screened area, an additional 50% to allow for settlement above screen casings, and the annular space between the borehole and the casing’s external diameter. | Job | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 0
1.6 | Water Well Development by airlifting (Compressor)for a minimum of 6 hours and until satisfactory yield is reached, stabilized turbidity is less than 5 NTU. and as per technical specfication, and standards,The documentation of the well development report should be submitted to IOM for verification and analysis. | Job | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 0
1.7 | Water Well Pumping Test: The Contractor will conduct an 8-hour step test with four different yields (Qmx/1, Qmx/2, Qmx/3, and Qmax), each lasting a minimum of 2 hours. A recovery test will follow, lasting until 90% of the static water level is recovered. Water levels will be measured at intervals of 1, 5, and 10 minutes for the first 120 minutes. After a minimum 12-hour gap, an 8-hour constant rate test will be conducted at a pumping rate agreed upon with the IOM Project Engineer, preferably at Qmax or 6m3/hr. A recovery test will follow, similar to the step test. All data from the step drawdown, constant pump test, and recovery should be reported on the IOM Pumping Test Log Sheet, including details like the position of the water level measurement datum, date of test, total depth of borehole, static water level before test, model of pump used, depth of pump intake, and discharge. The dynamic/pumping water level should also be recorded. | Job | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 0
1.8 | Supply and installation of a Submersible Solar Pump System: The Contractor will supply and install an off-grid type solar system with a submersible pump, capable of delivering a yield not less than the critical yield calculated after the pump test estimated capacity from 3 to 4 HP. The system will include all components such as Inverter/controller, cabling, uPVC rising pipe class 10 (min. diameter 50 mm), controller, submersible cable of at least 120m, float switch, adaptor set, surge protector, and lightning arrestor with a minimum of 1 piece of 3m copper‐plated grounding rod. the solar system pump, branded Lorentz or Groundfos, should be designed and approved by the IOM engineer, providing at least 4m3/hour total considering 8 peak sunshine hours. The off-grid solar panels will be mounted on the water tower/FHHs roof, tilted at 5-70 degrees, with the whole area protected by a fence. A mechanical flow meter will be installed for monitoring production also an automatic type float switch to stop the pump when the reservoir is full. Dry-run protection of the pump with automatic reset.* All components to be compliant with local water quality. * All components CE-approved | Job | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 0
1.9 | 50mm outside diameter HDPE PIPE PE 80: Supplying, fitting and fixing HDPE pipe conforming to the national standard, having the wall thickness 5.6-6.4mm, PN 10, compiling British standard BS-729 having hydrostatic test pressure minimum 50kg/cm2 (710 psi). all complete in all respects as per the direction of the E-I-C | m | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 270 | 0
1.1 | Trenches Excavation: Excavation of stone masonry of foundation trenches, including layout, by excavating earth to the lines, grades and elevation as shown in the drawing providing center lines, local bench mark pillars, fixing bamboo spikes and marking layout with chalk powder filling baskets, carrying and disposing of all excavated materials at a safe distance designated by the E-I-C in all types of soils including rocky, gravelly, slushy or organic soil, leveling, ramming, dressing and preparing the base, etc. all complete for an initial excavation depth of 3m, including arranging all necessary tools and equipment at work site, etc. complete as per direction of the E-I-C. Area at Water Supply project, but No.t limited within this. Refer Technical drawings of main gate. water well house room foundation plan , boundary wall and toliet technical specficiations under structural No.tes for method of works. | M3 | 0 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 129.6 | 0
1.11 | Back Filling with Soil: soil filling on the prepared foundation bed with sand of minimum FM 0.50 in difficult areas with maximum 150mm in thickness each layer including supplying, placing in conformity with the profile and level as per design including watering, compaction etc. all complete as per instruction of the Engineer-in-Charge. | M3 | 0 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 81 | 0
1.12 | Back Filling with Sand: Sand filling in foundation trenches and inside plinth with sand (minimum FM 1.20) in 150mm layers in/c leveling, watering and consolidating each layer up to finished level etc. all complete as per direction of the E-I-C. Dry density after compaction shall not be less than 95% of MDD (STD). | M3 | 0 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 48.6 | 0
1.13 | Water Well full physical, chemical, and bacteriological analysis Tests The contractor should follow the standard of WHO Guidelines for drinking water quality Test and it should be included as following but not limited to: Physical Parameters', TDS, ORP, Turbidity, PH and Temperature. Chemical Parameters: Alkalinity, Carbonate, Hydroxide, Chloride, sulphate, florid, Nitrate, Phosphate, Boron, Bromide, Iron, Lead, Manganese, Copper etc. Calcium, sodium, potassium, chromium, magnesium, ammonium, copper, aluminum, Iron, Arsenic, Uranium etc. Silica, Hydrogen sulphate, residual chlorine Bacteriological Parameters: Total coliform and fiscal coliform, etc. | Job | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 0
1.14 | Water Well disinfecation After collecting the water sample for testing, the borehole should be thoroughly disinfected with a chlorine-rich solution, preferably granular Calcium Hypochlorite (HTH) or Sodium Hypochlorite at a concentration of 500 grams per cubic meter of pack. This will initiate the process of sterilizing the borehole and the chlorine solution should stay in the borehole for at least 4 hours at the specified concentration, leaving a concentration of residual chlorine of 50 milligrams/liters (as per WHO standards). The disinfection procedure shall be discussed with IOM’s Project Engineer to seek approval. | Job | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 0
Sub Total | [13 empty] | 0
2 | Chamber of the Water Well
1.1 | Excavation: Earth work in excavation in different type area for foundation trenches or any other types of sub-structure including layout, providing center lines, local bench-mark pillars, levelling, ramming and preparing the base, fixing bamboo spikes and marking layout with chalk powder, providing necessary tools and plants, protecting and maintaining the trench dry etc., stacking, cleaning the excavated earth at a safe distance out of the area enclosed by the layout etc. all complete and accepted by the Engineer-in-charge, subject to submit method statement of carrying out excavation work to the Engineer-in-charge for approval. However, engineer’s approval shall not relieve the contractor of his responsibilities and obligations under the contract. | m3 | 0 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 7.344 | 0
1.2 | Burnt Brick masonry: Burnt Brick masonry: 250mm/350mm brickwork using 1st class bricks in cement mortar (1:4) anywhere with Portland Composite cement (CEM II/AM, 42.5N) and best quality sand (minimum FM1.2), filling the interstices tightly with mortar, raking out joints, cleaning and soaking bricks at least for 24 hours before use, washing of sand, curing for the requisite period preferred for at least 7 days, etc. all complete as per direction and approval of the E-I-C. | m3 | 0 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 2.45 | 22.05 | 0
1.3 | PCC with the concrete of M:(1:3:6): Mass concrete work in foundation or floor with Portland Composite Cement (CEM II/AM, 42.5N), sand (minimum FM 1.20) and 20mm down well graded stone chips (LAA value No.t exceeding 38), including shuttering, mixing by concrete mixer machine, casting, laying compacting with mechanical vibrator machine and curing for the requisite period crused stone chips etc. all complete as per direction of the E-I-C. Cylinder crushing strength of concrete should No.t be less than 10.5Mpa at 28 days of curing (suggested mix proportion 1:3:6). Additional quantity of cement to be added if required to attain the strength at the contractors own cost. P.C.C (1:3:6) under RCC foundation (Shifta) with all necessary requirements. | m3 | 0 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 0.816 | 7.344 | 0
1.4 | Reinforced Cement Concrete M20 (1:1.5:3): Reinforced cement concrete works including supply and fabrication of reinforcement rebars as per drawing, with minimum cement content relates to mix ratio (tentative 1:1.5:3) and maximum water cement ratio 0.4 having minimum required average strength, f'cr = 25 Mpa and satisfying a specified compressive strength f'c = 25 Mpa at 28 days on standard cylinders as per standard practice of Code AASHTO/ ASTM. Portland Composite Cement conforming to CEM-II 42.5N, best quality sand of minimum FM 2.50, 20mm well-graded crushed stone broken from boulder (LAA value not exceeding 30) conforming to ASTM C33 or any other internationally recognized standard. Cost includes of breaking and grading stone aggregate, screening through proper sieves, cleaning and washing thoroughly, centering, fully leak-proof shuttering works, placing of reinforcement in position, etc. Mixing in standard mixer machine as per approved mix design unless otherwise approved by the Engineer, fed by standard measuring boxes, maintaining allowable slump of 75mm to 100mm, compacting by mechanical vibrators and tapered rods and curing at least for 28 days, removing shuttering after approved specified time period, All complete as per direction and approval of the Engineer in charge. Note: Cost includes testing charges of materials and cylinders as required. | m3 | 0 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 0.825 | 7.425 | 0
1.5 | Plastering with Cement Sand Mortar 1:3, Minimum 12 mm thick cement sand (F.M. 1.2) plaster (1:3) with fresh cement to both inner-and outer surface of wall, finishing the corner and edges including washing of sand, cleaning the surface, curing at least for 7 days, cost of water, electricity, scaffolding and other charges etc. all complete in all aspects as per drawing and accepted by the Engineer-in-charge. (Cement: CEM-II/B-M). | m2 | 0 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 226.8 | 0
Sub Total | [13 empty] | 0
Grand Total | [13 empty] | 0
Note: This estimate is only for the purpose of predicting the volume of the project work and cannot be the final document of the project consumption, the real consumption of the project will be made based on the actual implemented volume of the work to the site, and final measurements.
Authorized Company Representative Name, Signature and Stamp