AGA KHAN HEALTH SERVICES-AFGHANISTAN

Request for Quotations (RFQ)

For

Procurement of: Solar System for Baghlan DH

Reference No.: RFQ/G/0164/2024

Issued By: Aga Khan Health Services – Afghanistan

30 July 2024

Table of Contents

1.	Invitation	3

2.	Instructions to Bidders	4

3.	Post Qualification Criteria	6

4.	Quotation Letter	7

5.     Quotations’ Price	8

6.	Specifications Of Goods	9

7.	Contract Agreement	10

8.     Performance Security	16

## Invitation

To: ……………………………………

Sub: 	Request for Quotation for Procurement of Solar System for Baghlan DH

Reference No.: RFQ/G/0164/2024

Dear Sirs,

- The Aga Khan Health Services (AKHS-A) intends to purchase the following goods (Solar System for Baghlan DH) and you are invited to submit your most competitive quotation for supply of the Goods as detailed in the Table below.

| Brief Description of Goods | Solar System for Baghlan DH |
| --- | --- |
| Quantity | 25 |
| Specifications | Please refer to section 6 |
| Delivery Period | Within 30 calendar days starting one day after contract signing date. |
| Sample check | AKHS-A National Programe office, House 42, Behind Kabul Municipality Apartments, Klola Pushta, District 4, Kabul, Afghanistan |
| Place of Delivery | Baghlan Province – District Hospital (Baghlan Jadid) |

- To assist you in the preparation of your quotation, we are enclosing the following:

- Instructions to Bidders.

- Specification of the Goods.

- Your quotation using the attached Form should be submitted duly in a sealed envelope and delivered at the following address: House 42, Behind Kabul Municipality Apartments, Klola Pushta, District 4, Kabul, Afghanistan

- The quotation submitted by the bidder shall comprise the following:

- Quotation using the Form.

- Qualification Information enclosed in this document.

- A bid security (not applicable)

- Bid security declaration form. and

- Similar contract with the total value of 1,500,000 AFN which was Completed during the last five years.

- The deadline for receipt of the quotations by the AKHS-A at the address stipulated in Para 3 above is 4th Aug 2024 at 10:00 AM Kabul Local Time.

- Quotations received after the deadline will be rejected.

Yours sincerely,

(AKHS-A)

Signature: ............................................

## Instructions to Bidders

- Scope of Supply

The AKHS-A invites quotations for the supply of Goods as detailed in the Table below.

| Brief Description of Goods | Solar System for Baghlan DH |
| --- | --- |
| Quantity | 25 |
| Specifications | Please refer to section 6 |
| Delivery Period | Within 30 calendar days starting one day after contract signing date |
| Sample check | AKHS-A National Programe office, House 42, Behind Kabul Municipality Apartments, Klola Pushta, District 4, Kabul, Afghanistan |
| Place of Delivery | Baghlan Province – District Hospital (Baghlan Jadid) |

The successful Bidder will be expected to complete the delivery of Goods within the Delivery Period specified above.

- Bid Price

(a) 	The Quotation shall be submitted for the full quantity as described above.

(b)	All duties, taxes, and other levies payable shall be included in the total price.

(d)	Prices quoted by the bidder shall be fixed for the duration of the contract and shall not be subject to adjustment on any account.

(e)	The Prices shall be quoted in Afghani only.

- Submission of Quotations

4.1	Each Bidder shall submit only one quotation.

4.2	The Bidder shall seal the quotation in an envelope addressed to the AKHS-A     as per address provided in Para 3 of the Letter of Request for Quotation.

4.3.	The envelope shall bear the following identification:

  - Quotation for Solar System for Baghlan DH

  - Reference No.: RFQ/G/0164/2024

  - Name and address of the Bidder: ________________________________

4.4	Quotations must be received in AKHS-A’s office not later than the deadline stipulated in the Letter of Request for Quotation. If the specified date is declared a holiday for the AKHS-A, quotations shall be received up to and opened at the appointed time on the next working day.

4.5	Any quotation received after the deadline for submission will be rejected and returned unopened to the Bidder.

- Validity of Quotation

Quotation shall remain valid for a period not less than 30 days after the deadline specified for submission.

- Confidentiality

Information relating to evaluation of quotations and recommendations for the award of contract shall not be disclosed to bidders or any other persons not officially concerned with the process until the award to the successful Bidder is made.

- Evaluation of Quotations

The AKHS-A will evaluate and compare the quotations determined that:

- meet the qualification criteria specified in clause 2 above.

- are properly signed; and

(c)	conform to the terms and conditions, and specifications without                    material deviations.

7. The Quotations would be evaluated for all the items together.

7.1 	In evaluating the quotations, the AKHS-A will determine for each quotation the evaluated price by adjusting the quoted price by making correction for any arithmetic errors as follows:

(a) 	where there is a discrepancy between amounts in figures and in words, the amount in words will govern.

(b) 	where is a discrepancy between the unit rate and the line-item total resulting from multiplying the unit rate by the quantity, the unit rate as quoted will govern.

7.2 	Bidders shall be requested to accept correction of arithmetical errors. Failure     to accept the correction shall result in the disqualification of the quotation and the Bidder will be declared ineligible to be awarded a contract by AKHS-A for a period of at least one year.

8. Award of contract

8.1	The AKHS-A will award the contract to the Bidder whose quotation has been determined to be substantially responsive and who has offered the lowest evaluated price and who meets the specified qualification criteria.

8.2	Notwithstanding the above, AKHS-A reserves the right to accept or reject any quotations and to cancel the bidding process and reject all quotations at any time prior to the award of contract.

8.3	The Bidder whose Quotation is accepted will be notified of the award of contract / issuance of a Purchase Order (PO) by the AKHS-A prior to expiration of the quotation validity period.

- Payment for Supply

Payment shall be made within 30 days after the successful delivery of all the Goods.

- Warranty/Guarantee:

One year warranty of all Goods.

## Post Qualification Criteria

Qualification Criteria

- Prior to the Contract Award /Purchase Order issuance, the supplier whose bid has determined to be the lowest and technically responsive, will be invited to bring the samples of the quoted items, the same will be checked and verified by the AKHS-A's technical team. If the samples are not accepted by the technical team, then the supplier will be disqualified and the 2nd (3rd, 4th ...) lowest and technically qualified bidders will be invited for the process by sequence. (N/A)

- The supplier must submit one completed contract of a similar nature with a total value of 1,500,000 AFN, which was completed during the last five years. The submission should include detailed information about the client.

e.g. official email address of the client.

## Quotation Letter

To: AKHS-A

Subject:  Procurement of Solar System for Baghlan DH

Reference:	 RFQ/G/0164/2024

Dated:  	…………………….

Dear Sir,

- We offer to supply the Goods (Solar System for Baghlan DH) described in your letter referred to above in accordance with the Specifications enclosed therewith for a total price as under:

AFN _________________________________________________ [in figures]

AFN _________________________________________________ [in words]

- We will complete the Supply of Goods (Solar System for Baghlan DH) offered by us within the Delivery Period specified in the Request for Quotation document.

- We will supply the Goods (Solar System for Baghlan DH) as per specification enclosed with the Request for Quotation without any deviations.

- This quotation and your written acceptance thereof shall constitute a binding contract with us. We understand that you are not bound to accept the lowest or any quotation you receive.

- We certify that we have not been debarred or suspended from participation in bidding by any Procuring Entity of the Islamic Republic of Afghanistan or by AKDN agencies.

- We hereby confirm that our quotation shall remain valid for the period as specified in clause number 9 above.

Yours faithfully,

Authorized Signature 		 _____________________________________________

Date				 ______________

Name & Title of Signatory	 _____________________________________________

Name of Company		 _____________________________________________

Address			 _____________________________________________

_____________________________________________

## Quotations’ Price

Procurement of: Solar System for Baghlan DH

RFQ No: RFQ/G/0164/2024

| SN | Description of items | Unit | Quantity | Unit Cost (AFN) | Sub-total Cost (AFN) |
| --- | --- | --- | --- | --- | --- |
| 1 | 550 W - Solar Panels or higher wattage, Brand: JA, Trina, Jinko having certified Test Reports from Tier-1 and A-grade Brands. It should have half cut/cell technology (Item brand would be from consultant list). | Pc | 50 |  |  |
| 2 | 10KW hybrid inverter, Brand: Growatt | Pc | 3 |  |  |
| 3 | DC Cables 1X6 mm2 | M | 600 |  |  |
| 4 | Battery bank, Brand: RITAR Vietnam or SAITE (AGM Deep cycle) (12V, 200Ah), battery bank including battery rack | Pc | 8 |  |  |
| 5 | PV frame from GI U-Channel under PV panels 1.5mm and 1mm GI U-channel under panel for cable series connection of panels, and Hot-Dipped Galvanized Angled Iron 60x60x5 mm (for vertical stands) and 50x50x5 mm for horizontal support and base frame including rubber insulation (between U-Channel and PV panel). | Pc | 50 |  |  |
| 6 | PVC coated flexible Galvanized steel pipe 1.5 inch and 0.5 inch | M | 150 |  |  |
| 7 | Cable Tray Galvanized as per standard Design | M | 40 |  |  |
| 8 | Connector, Cable Tie and other accessories | Ls | 1 |  |  |
| 9 | Conduit ( PVC) | LS | 1 |  |  |
| 10 | Air condition for control room | set | 1 |  |  |
| 11 | Grounding system with 16mm, 10mm and 4 mm also 2.5mm, copper cables connected to all of the facilities and equipment, installation of lighting arrestor- system shall have maximum earthing resistance of 5 ohm or lower and must perform grounding test. | Ls | 1 |  |  |
| 12 | Cable 1x25 sqmm | M | 60 |  |  |
| 13 | Cable 4x6 sqmm | M | 100 |  |  |
| 14 | main cable flexible cable for different room connection like NICU, delivery and OT (4x25mm), | M | 150 |  |  |
| 15 | Busbar | M | 4 |  |  |
| 16 | DC Fuse | Set | 1 |  |  |
| 17 | Dc breaker | set | 1 |  |  |
| 18 | AC Fuse box | set | 1 |  |  |
| 19 | ATS system for the automatic switching between solar system, Govt electricity, existing generator and future power bank, the system should be capable of automatically switching On/Off the generator also the ATS should be connected to the existing power system. | Set | 1 |  |  |
| 20 | RCC for the foundation of PV frame with 16mm galvanized anchor bolts and 250x250x10mm steel plate for each leg | Ls | 1 |  |  |
| 21 | on site visit and Survey and Design including shadow analysis and PV Analysis Reports for PV System. Design of Structure and its analysis report of E-Tabs and Submission of As-Built Drawings according to Standards | Ls | 1 |  |  |
| 22 | Monitoring and repair services and services for one year | Ls | 1 |  |  |
| 23 | Installation, Testing, Commissioning and training for electrician | Ls | 1 |  |  |
| 24 | Preparation of room for inverters including plastering, painting, ducting etc. | LS | 1 |  |  |
| 25 | Transportation | Ls | 1 |  |  |
| Grand Total Price (in AFN) |  |  |  |  |  |

Supplier Name: _______________________________________

We agree to supply the Goods (Solar System for Baghlan DH) in accordance with the Specifications for a total price of AFN.............................................................................. (amount in figures).

Prices quoted above are inclusive of all duties and taxes.

Signature and Stamp: ……………………………………………….

## Specifications Of Goods

| S.N. شماره | Item Name اسم جنس | Required Specification مشخصات | Bidder’s Response Comply / Not-Comply قبولی یا عدم قبولی داوطلب |
| --- | --- | --- | --- |
| 1 | 550 W - Solar Panels or higher wattage, Brand: JA, Trina, Jinko having certified Test Reports from Tier-1 and A-grade Brands. It should have half cut/cell technology (Item brand would be from consultant list). | 12–15-year product warranty, 25–30-year linear warranty for accepted international brands. If higher wattage, then Qty. may vary or decrease. |  |
| 2 | 10KW hybrid inverter, Brand: Growatt | Hybrid inverter should be 10 KW and Qty may differ if higher wattage quoted. But the wattage of inverter should not be less than 10KW. Available all advance and necessary features including, user manual, service manual, WI-FI access (WIFI KIT) and update version software also should part of it, 5-year product warranty. |  |
| 3 | DC Cables 1X6 mm2 | DC Cables 1X6 mm2 from PV panels to inverter - Turkish made |  |
| 4 | Battery bank, Brand: RITAR Vietnam or SAITE (AGM Deep cycle) (12V, 200Ah), battery bank including battery rack | (1) 12V, 200 - 230 Ampere, (2) Gel Battery, (3) At least 3-5 years warranty and 10 years linear life (4) it should be 2800 life cycles at 50% DOD, battery bank needs to include battery rack for 12 battery, battery rack including Hot-dipped galvanized angled iron 60x60x5mm, insulation rubber, Lasonya Turkish plywood 18mm best quality. |  |
| 5 | PV frame from GI U-Channel under PV panels 1.5mm and 1mm GI U-channel under panel for cable series connection of panels, and Hot-Dipped Galvanized Angled Iron 60x60x5 mm (for vertical stands) and 50x50x5 mm for horizontal support and base frame including rubber insulation (between U-Channel and PV panel). | All materials must be Hot-Dipped galvanized |  |
| 6 | PVC coated flexible Galvanized steel pipe 1.5 inch and 0.5 inch | Turkish made, for electric cables from roof-top to powerhouse (outside) |  |
| 7 | Cable Tray Galvanized as per standard Design | For inside power rooms and for between two buildings, for better cable management with different size (30cmx5cm and 20cmx5cm) or as per side need. |  |
| 8 | Connector, Cable Tie and other accessories | All kind of connector is responsibility of the contractor |  |
| 9 | Conduit (PVC) | For Protecting of wires and good visibility made, need to provide different size as per side requirements. |  |
| 10 | Air condition for control room | Digital-inverter type, original air condition, cooling and heating option available as per room size needed, also available exhaust with ventilation, (12000BTU). |  |
| 11 | Grounding system with 16mm, 10mm and 4 mm also 2.5mm, copper cables connected to all the facilities and equipment, installation of lighting arrestor- system shall have maximum earthing resistance of 5 ohm or lower and must perform grounding test. | 16mm main out-going (from panel board main junction to grounding well), 10mm (from PV panel main junction to control room), 4mm (between inverter and distribution board) and 2.5mm (from all PV panels to junction box), Rod cupper clad steel 3m with 20mm Dia, (Qty-3 rods). |  |
| 12 | Cable 1x25 sqmm | DC cable for connection of batteries and batteries to inverter, pure copper wire made in Turkish. |  |
| 13 | Cable 4x6 sqmm | AC cable 4x6mm2 for connecting the inverter to distribution panel, pure copper wire, Turkish made, best quality |  |
| 14 | main cable flexible cable for different room connection like NICU, delivery and OT (4x25mm), | This cable can be further re-visited during site visit and can proposed as per site need. Cable should be flexible 4/5 core Turkish brand |  |
| 15 | Busbar | Cupper Bus bar 40x5mm |  |
| 16 | DC Fuse | DC, 2 Pole, 250 Ampere- between inverter and battery, best quality, Made-in Turkish |  |
| 17 | Dc breaker | Dc, 2 pole, 20 Ampere-between solar and inverter brand: Schneider or Turkish brand including fuse box |  |
| 18 | AC Fuse box | As per site need with complete circuit breakers (Sigma, ABB or Federal) including Panel board with size (100x150x40) cm, measuring and signaling system for all incoming and outgoing. |  |
| 19 | ATS system for the automatic switching between solar system, Govt electricity, existing generator and future power bank, the system should be capable of automatically switching On/Off the generator also the ATS should be connected to the existing power system. | ATS (100 Ampere or higher with relay as per side need) or higher Turkish brand (or as per need) and EMS including battery bank (ON/OFF) of generators automatically controlled |  |
| 20 | RCC for the foundation of PV frame with 16mm galvanized anchor bolts and 250x250x10mm steel plate for each leg | Proper foundation as per structure need and design, with proper galvanized anchor bolts, steel plate and other accessories including steel cable for holding |  |
| 21 | On-site visit and Survey and Design including shadow analysis and PV Analysis Reports for PV System. Design of Structure and its analysis report of E-Tabs and Submission of As-Built Drawings according to Standards | E-tab software is automatically analysis of steel structure not to disturb load of PV. All reports to be submitted to AKHS. |  |
| 22 | Monitoring and repair services and services for one year | In each month, the contractor is bound to visit the site at least one time to monitor and repair and maintenance of PV panels, inverters and other related items for the period of one year. But in any problem, the contractor is bound to urgently visit the site and do the proper repair and replace any damaged part free of cost during the warranty period. contractor is also bound to do maintenance/service free of cost during overall warranty period which is one year. Warranty period start date would be after complete installation of the system and tested. |  |
| 23 | Installation, Testing, Commissioning and training for electrician | All is the responsibility of the contractor. Certificate for electrician to be provided. |  |
| 24 | Preparation of room for inverters including plastering, painting, ducting etc. | room plastering, painting and related renovation should be included |  |
| 25 | Transportation | All kind of transportation is responsibility of contractor till site. |  |
|  |  | Signature and Stamp: ………………………………………………. |  |

## Essential Notes:

- AKHS, A has the right to increase/decrease the quantity of the items/services mentioned.

## Bid-Securing Declaration Form

Date: 30/07/2024

Reference No: RFQ/G/0164/2024

Package Name: Solar System for Baghlan DH

To: Aga Khan Health Services – Afghanistan

Dear Sir,

We, the undersigned, declare that:

We understand that, according to your conditions, bids must be supported by a Bid-Securing Declaration.

We accept that we will automatically be suspended from being eligible for bidding in any contract with the AKHS-A for the period of (One Year effective from the date of our withdrawal), if we are in breach of our obligation(s) under the bid/quotation conditions, because we:

(a) 	have withdrawn our Bid during the period of bid validity specified in the Form of Bid; or

(b) 	having been notified of the acceptance of our Bid by AKHS-A during the period of bid validity, (i) fail or refuse to execute the Contract, if required, or (ii) fail or refuse to furnish Performance Security.

We understand this Bid Securing Declaration shall expire if we are not the successful Bidder and the contract is awarded to other suppliers.

Name: ……………………………………………

Position: …………………….……………………

Signed: ……………………………………………

Contract Agreement

Contract Data

| SN | Item | Contract Data |
| --- | --- | --- |
| 1 | Contract Number and name |  |
| 2 | Contract Date |  |
| 3 | Name and Address of the Supplier |  |
| 4 | Description of Goods ordered |  |
| 5 | Quantity |  |
| 6 | Place of Delivery |  |
| 7 | Contract Price (including all applicable taxes) |  |
| 8 | Supplier’s Bank Account details |  |
| 9 | Payment Terms / Installments |  |
| 10 | Delivery due date |  |

This Agreement is made on the date specified in the Contract Data by and between the AKHS-A and ……………………… “Called as Supplier” holds its business address as mentioned above.

Whereas the AKHS-A is desirous that the Supplier shall execute the Contract as stated in the Contract Data and the AKHS-A has accepted the Quotation submitted by the Supplier, the Contract shall be governed by the conditions stipulated herein.

a: The price list and specifications are attached with the contract.

CONDITIONS OF CONTRACT

1.	Language and Law

The Contract shall be in the English. The law governing the Contract shall be the applicable law(s) of the Afghanistan government.

2.	Communications

Communications between parties that are referred to in these Conditions shall be effective only when made in writing.  A notice shall be effective only when it is delivered.

3.	Delivery Period

Supply shall be delivered within the Delivery Period stipulated in the Contract Data and delivery location as specified in the RFQ.

4.	Scope of Supply

The Goods (Solar System for Baghlan DH) shall be supplied as per Specifications indicated in part # 5.

5. 	Price

Contract Prices detailed in the Contract Data shall be fixed and shall not be subject to adjustment on any account.

6. 	Taxes

The Supplier shall be entirely responsible for all taxes, duties, license fees, etc., incurred until/for the delivery of the contracted Goods (Solar System for Baghlan DH) to the AKHS-A.

7.	Payments

Payments shall be made by the Finance Department of AKHS-A directly to the company’s bank account. If the company does not currently have a bank account, it is highly recommended to open one, preferably at The First Micro Finance Bank of Afghanistan (FMFB-A). Payments will be processed within thirty (30) days after the successful delivery of the goods, their acceptance by AKHS-A, and the submission of an invoice or payment request by the supplier.

However, 5% of the total contract amount shall be retained by AKHS-A until the warrantee period is completely accomplished.

8.  	Performance Security (N/A)

8.1 	The Contractor shall provide to the AKHS-A Performance Security equal to five (5) % of the Contract Price within 10 days of receiving Notification of Award/Letter of Acceptance in the form of a bank guarantee included in Section 3.

8.2 	The Performance Security shall be valid until 28 days beyond the completion of contract obligations including Warranty Period and shall be released to the Supplier on satisfactory correction of the Supplier’s performance obligations under the Contract, including Warranty obligations.

8.3	In the event of termination of the contract for fundamental breach of the Contract by the supplier, the Performance Security shall be forfeited.

9.	Warranty

9.1 	Supplier warrants that the Goods shall be free from defects arising from any act or omission of the Supplier or arising from design, materials, and workmanship, under normal use in the conditions prevailing in the final destination.

9.2	The warranty shall remain valid for 1 year after the Goods, or any portion thereof as the case may be, have been delivered to and accepted at the final destination.

9.3 	The AKHS-A shall give notice to the Supplier stating the nature of any such defects promptly following the discovery thereof.  The AKHS-A shall afford all reasonable opportunity for the Supplier to inspect such defects. Upon receipt of such notice, the Supplier shall, within 4 days repair or replace the defective Goods or parts thereof, at no cost to AKHS-A.

10.	Termination for Default

The AKHS-A, without prejudice to any other remedy for breach of Contract, by written notice of default sent to the Supplier, may terminate the Contract in whole or in part:

- if the Supplier fails to deliver any or all of the Goods within the period specified in the Contract, or within any extension thereof granted by the AKHS-A ;

- if the Supplier fails to perform any other obligation under the Contract; or

- if the Supplier, in the judgment of the AKHS-A has engaged in fraud and corruption, in competing for or in executing the Contract.

- The subcontractor agrees to implement policies prohibiting Sexual Exploitation and Abuse (SEA) and to take measures for prevention and response. This includes staff training, confidential reporting mechanisms, survivor support services, investigation cooperation, and regular monitoring. Failure to comply may result in contract termination.

11. 	Resolution of Disputes

11.1	The AKHS-A and the Supplier shall make every effort to resolve amicably by direct negotiations any disagreement or dispute arising between them under or in connection with the Contract.  In case of further disagreement either party can take the matter to arbitration. The Arbitrator will be nominated by the AKHS-A leadership. The place where arbitration will take place will be Kabul, Afghanistan.

11.2 	Arbitration proceedings will be governed by latest Afghanistan Commercial Arbitration Law.

12.	Liquidated Damages

12.1 	If the Supplier fails to deliver any or all of the Goods by the Date(s) of delivery or perform the Related Services within the period specified in the Contract, the AKHS-A will deduct from the Contract Price, as liquidated damages, a sum equivalent to the percentage as below.

a) 0.1%/day of the total contract price.

b) The maximum amounts of charges as liquidated damages shall be: 10 % of the contract value. Once the maximum is reached, the AKHS-A may terminate the Contract with the Supplier.

13.	Force Majeure

13.1	The Supplier shall not be liable for forfeiture of its Performance Security, liquidated damages, or termination for default if and to the extent that its delay in performance or other failure to perform its obligations under the Contract is the result of an event of Force Majeure.

13.2	For purposes of this Clause, “Force Majeure” means an event or situation beyond the control of the Supplier that is not foreseeable, is unavoidable, and its origin is not due to negligence or lack of care on the part of the Supplier.  Such events may include, wars or revolutions, fires, floods, epidemics, quarantine restrictions, and freight embargoes.

13.3	If a Force Majeure situation arises, the Supplier shall promptly notify AKHS-A in writing of such condition and the cause thereof.  Unless otherwise directed by the AKHS-A in writing, the Supplier shall continue to perform its obligations under the Contract as far as is reasonably practical and shall seek all reasonable alternative means for performance not prevented by the Force Majeure event.

In Witness whereof the parties thereto have caused this Agreement to be executed the day, month and year written hereunder:

Signed, sealed, and delivered by the said Parties:

| Signature on behalf of AKHS-A | Signature on behalf of the Supplier |
| --- | --- |
| Signature: ………………………………. | Signature: ……………………… Stamp: ………. |
| Name...................................... | Name............................................ |
| Date....................................... | Date............................................. |
| Designation........................... | Designation................................... |

## Performance Security (N/A)

(Bank Guarantee)

Beneficiary:	Aga Khan Health Services – Afghanistan

Date:	………………….

PERFORMANCE GUARANTEE No.:	[Insert guarantee reference number]

Guarantor: [Insert name and address of place of issue, unless indicated in the letterhead]

We have been informed that _ [insert name of Supplier] (hereinafter called "the Applicant") has entered Contract No. [insert reference number of the contract] dated [insert date] with the Beneficiary, for the execution of _ [insert name of contract and brief description of Works] (hereinafter called "the Contract").

Furthermore, we understand that, according to the conditions of the Contract, a performance guarantee is required.

At the request of the Applicant, we as Guarantor, hereby irrevocably undertake to pay the Beneficiary any sum or sums not exceeding in total an amount of [insert amount in figures] (______) [insert amount in words], such sum being payable in the types and proportions of currencies in which the Contract Price is payable, upon receipt by us of the Beneficiary’s complying demand supported by the Beneficiary’s statement, whether in the demand itself or in a separate signed document accompanying or identifying the demand, stating that the Applicant is in breach of its obligation(s) under the Contract, without the Beneficiary needing to prove or to show grounds for your demand or the sum specified therein.

This guarantee shall expire, no later than the 30 Day of ……,2024, and any demand for payment under it must be received by us at this office indicated above on or before that date.

_____________________ 
[signature(s)]

Note:  All italicized text (including footnotes) is for use in preparing this form and shall be deleted from the final product.