## DATA1
ID#: | A221873
Province: | Faryab
District : | Dawlat Abad
Village : | Jar Qala
Project Purpose: Construction of Solar Powered Water Supply Network
Total Length of Pipe (m) | 4018
Number of meters | 110
Volume of reservoir (M3) | 40
Targeted papulation 197 Family, 1379 People
197

## Estimation
Project: |  |  |  | province | Faryab |  | Date:
ID# |  |  |  | district | Dawlat Abad
Project purpose: cosntruction of sorlar powered water supply network |  |  |  | village | Jar Qala
S/N | Particulars of Items شرح موضوع | No. تعداد | Area مساحت |  | Length طول | Legth or Depth. طول یا صخامت | Qty مقدار | Total Qty مقدارمجموعی | Unit مقدار
1 | Site prepration | [6 empty] | 435 | M2
1.01 | Site prepration solar area, and well | 1 | a*b | 20 | 20 | - | 400 | 400 | M2
1.03 | Site preparation for Reservoir | 1 | a*b | 5 | 7 | - | 35 | 35 | M2
2 | Excavation | [6 empty] | 1448.56 | M3
2.01 | Excavation for pipe scheme | 1 | b*h*L | 0.4 | 0.8 | 4018 | 1285.76 | 1285.76 | M3
2.02 | Excavation for on the RCC storage reservoir | 1 | b*L*d | 4 | 7 | 3.35 | 93.8 | 93.8 | M3
2.02 | Excavation for on the Valve Box of reservoir | 1 | b*L*d | 2 | 2 | 1.05 | 4.2 | 4.2 | M3
| Solar Panel Stand | 3 | b*L*d | 1 | 1 | 1 | 1 | 3 | M3
2.03 | Excavation for water point | 110 | b*L*d | 1 | 1.5 | 0.2 | 0.3 | 33 | M3
2.05 | Excavation for foundation for Fencing | 1 | b*L*d | 0.6 | 0.6 | 80 | 28.8 | 28.8 | M3
3 | PCC 150 (1:2:4) | [6 empty] | 27.09 | M3
3.01 | PCC of water reservoir Footing | 1 | b*h*t | 4 | 7 | 0.1 | 2.8 | 2.8 | M3
3.02 | PCC of water reservoir top slab | 1 | b*h*t | 6.4 | 3.4 | 0.1 | 2.176 | 2.176 | M3
| PCC of water point stand | 110 | b*h*t | 0.01 | 0.7 | 1 | 0.007 | 0.77 | M3
| PCC of water point apron | 110 | b*h*L | 0.84 | 0.84 | 0.1 | 0.07056 | 7.7616 | M3
| Solar Panel Stand | 3 | b*h*L | 1 | 1 | 1 | 1 | 3 | M3
3.03 | PCC of water point apron walls | 110 | b*h*L | 0.08 | 3.74 | 0.2 | 0.05984 | 6.5824 | M3
3.05 | PCC of fencing top of stone masonry | 1 | b*t*L | 0.5 | 0.1 | 80 | 4 | 4 | M3
4 | RCC 250 (1:1:2) |  | b*h |  |  |  |  | 23.6948 | M3
4.01 | RCC of Water reservoir for Footings | 1 | a*b*c | 0.2 | 0.4 | 16.4 | 1.312 | 1.312 | M3
4.02 | RCC of Water reservoir Bottom Slab | 1 | a*b*c | 6.4 | 3.4 | 0.2 | 4.352 | 4.352 | M3
4.03 | RCC of Water reservoir Top Slab | 1 | a*b*c | 6.4 | 3.4 | 0.15 | 3.264 | 3.264 | M3
4.03 | RCC of Water reservoir Walls | 1 | a*b*c | 19.6 | 2.8 | 0.2 | 10.976 | 10.976 | M3
4.04 | RCC of Water Storage Valve Box Under Box+Top of Slab | 6 | a*b*c | 1.3 | 1.3 | 0.15 | 0.2535 | 1.521 | M3
4.04 | RCC of Water Storage Valve Box Walls | 3 | a*b*c | 5.2 | 0.97 | 0.15 | 0.7566 | 2.2698 | M3
5 | Stone Masonry (M200 Mortar 1:4) | [6 empty] | 40 | M3
5.01 | Stone masonry work under fencing 1 Under Ground | 1 | b*h*L | 0.5 | 0.5 | 80 | 20 | 20 | M3
5.02 | Stone masonry work under fencing 2 Over Ground | 1 | b*h*L | 0.5 | 0.5 | 80 | 20 | 20 | M3
6 | Pointing - M350 | [6 empty] | 80
6.01 | Poinging Work for under fencing 1 Under Ground | 2 | b*h | 0.5 | 80 |  | 40 | 80 | M2
6.02 | Poinging Work for under fencing 2 On the Ground | 0 | b*h | 0.4 | 2.5 | - | 1 | 0 | M2
7 | Painting | [6 empty] | 49
7.01 | Painting for the water point | 0 | b*L | 7.6 | 2 | - | 15.2 | 0 | M2
| Painting for the reservoir | 1 | b*L | 19.6 | 2.5 | - | 49 | 49 | M2
8 | Plaster with Water Proof Powder | [6 empty] | 72.16
8.01 | Waterproof Powder Plaster for the water reservoir | 1 | a*b | 16.8 | 3 | - | 50.4 | 50.4 | M2
8.02 | Waterproof Powder Plaster for floor of the reservoir | 1 | a*b | 6.4 | 3.4 | - | 21.76 | 21.76 | M2
8 | Isogam | [6 empty] | 24.5
8.01 | Isogam for roof insulation of the water reservoir | 1 | a*b | 3.5 | 7 | - | 24.5 | 24.5 | M2
8 | Shuttering | [6 empty] | 153.6
8.01 | Shuttering for Water Reservoir Wall | 2 | P*h | 19.6 | 3 | - | 58.8 | 117.6 | M2
8.02 | Shuttering for Water Reservoir Top Slab | 1 | b*w | 6 | 4 | - | 24 | 24 | M2
8.07 | Shuttering for footing of Solar Stand | 3 | b*h | 4 | 1 | - | 4 | 12 | M2
9 | Reinforcement | dia | L*kg/L | L (m) | kg/L | 1 | kg | 2896.5399
9.01 | Reinforcement for the Water Reservoir | 10 | L*kg/L | 726.4 | 0.6166 | 1 | 447.8982 | 470.2932 | KG
|  | 12 | L*kg/L | 1190.9 | 0.888 | 1 | 1057.5192 | 1110.3952 | KG
|  | 16 | L*kg/L | 604 | 1.578 | 1 | 953.112 | 1000.7676 | KG
9.04 | Reinforcement for footing of Solar Stand | 14mm | L*kg/L | 31 | 1.21 | 8 | 300.08 | 315.084 | KG
10 | Earthwork (Backfilling with soil and compaction) | [6 empty] | 1330.156
10.01 | Earthwork Backfilling for water reservoir | 1 | P*w*d | 19.6 | 0.3 | 1.7 | 9.996 | 9.996 | M3
10.02 | Earthwork Backfilling for pipe scheme | 1 | b*h*L | 0.4 | 0.8 | 4018 | 1285.76 | 1285.76 | M3
10.03 | Earthwork Backfilling for foundation of Solar Stand | 3 | b*h*L | 0.2 | 4 | 1 | 0.8 | 2.4 | M3
10.04 | Earthwork Backfilling for foundation for Fencing | 2 | b*h*L | 0.2 | 1 | 80 | 16 | 32 | M3
10.06 | Eearth Backfilling for fencing foundation | 0 | b*h*L | 0.9 | 0.8 | 80 | 57.6 | 0 | M3
11 | Graveling | [6 empty] | 36.538
11.02 | Graveling under for Well Apron | 1 | b*L*t | 1.2 | 1.2 | 0.2 | 0.288 | 0.288 | M3
| Compacted clean river gravel under the stand taps | 110 | b*L*t | 1 | 1.5 | 0.05 | 0.075 | 8.25 | M3
| Gravelling for fencing area | 1 | b*L*t | 20 | 20 | 0.07 | 28 | 28 | M3
WV Review Committee Members and RRD Representative Signatures/امضای اعضای کمیته برسی دفتر ورلدویژن وریاست انکشاف دهات
Project Engineer/انجینرپروژه
| Project Manager/مسؤل پروژه |  |  |  | Zone Manager/ مسؤل دفتر ساحوی ورلدویژن
| CDC/شورای انکشافی قریه |  |  |  | DRRD/رییس ریاست احیاً و انکشاف دهات

## Sheet1
Project purpose: cosntruction of sorlar powered water supply network |  | village | Jar Qala
project: DAWAM |  | Project # : | A221873 | Date:
Province: | Faryab | District | Dawlat Abad
NO | ITEMS موضوعات | UNIT واحد | Work quantity and cost estimated برآورد احجام کاری
|  |  | QUANTITY مقدار | Unit Cost (Af) قیمت فی واحد | Total cost(Afs) قیمت مجموعی
1 | Site Preparation: to clean site from all existent materials. | M2 | 435
2 | Excavation: In ordinary soil-type three, excavation will be take place types 4 | M3 | 1448.56
3 | PCC (M-150, 1:2:4): The PCC work is for plecement under the collecting stand according to the drawing considering the shuttering needs, using cement sand mortar base on given specifications. • Curing should be done for minimum 7 days. | M3 | 27.09
4 | Stone masonry 1:5: Providing and laying stone masonry with (35-40) % cement sand mortar 1:5, and it must include all good stone constrcution specification and site engineer satisfaction. | M3 | 40
5 | Pointing - M400 1:3: Pointing of all the joints of stone mosanry work with sandy clay mortor of M400 specification. The pointing should be uniformed and well curing is needed as per drawing and specification. | M2 | 80
6 | RCC- M250 (1:1:2) Crushed gravel must be used, and curing must be continued up to one month, and all site engineer advicess must be considered. | M3 | 23.6948
7 | Shuttering: The shuttering should be done as per the drawing and specification, as according to site engineer advice. | M2 | 153.6
8 | gravelling according to the drawings and specificatioon. | M3 | 36.538
9 | Painting: The work should be get done in proper way as per the drawing and specification any input of the site engineer. | M2 | 49
Plaster with water proof powder
10 | Plaster with water proof powder | m2 | 72.16
BackFilling
11 | Back filling as technical required | M3 | 1330.156
12 | Fencing Posts and mesh with 2.4m door including transportaion and installation cost | L.M | 80
GI Pipe and Fittings for RCC Water Reservoir
13 | Galvanized Iron (GI) pipe, for Drain pipe, wall thickness 2.6 mm ,weight 2.9 kg/m, Nominal Diameter 1 1/2",. | m | 3
14 | GI-pipe 3" Outlet Pipe with Glass Wool | m | 2
15 | Galvanized Iron (GI) pipe, for over flow pipe, wall thickness 2.9 mm ,weight 5.18 kg/m, Nominal Diameter 2 1/2",. | m | 3
16 | Galvanized Iron (GI) pipe,wall thickness 2.6 mm ,weight 2.9 kg/m, Nominal Diameter 1 1/2" ventilation of W.R | m | 3
17 | GI-pipe 3" Inlet Pipe with Glass Wool | m | 3
| Galvanized Iron (GI) pipe,wall thickness 2.6 mm ,weight 2.9 kg/m, Nominal Diameter 1 1/2" ventilation of W.R | m | 3
18 | GI-Nipple 3" | PCS | 8
19 | Union 3" | PCS | 6
20 | PE adapter 75mm to 2 1/2" | PCS | 2
21 | Gate Valve 3" stainless steel | PCS | 1
| Gate Valve 2 1/2" stainless steel | PCS | 1
22 | Teflon tape, thread seal tape shall. | PCS | 4
23 | Skilled labour on site | md | 0.5
GI Pipe and Fittings for valve box
24 | Galvanized Iron (GI) pipe, wall thickness 2.9 mm ,weight 5.18 kg/m, Nominal Diameter 2 1/2",. | m | 6
25 | GI-Nipple 2 1/2 " | m | 4
26 | Union 2 1/2 " | m | 4
27 | PE adapter 75mm to 1 1/2 " | m | 4
28 | Gate Valve 2 1/2 " stainless steel | PCS | 4
29 | GI-pipe 2 1/2 " | PCS | 6
30 | GI-Nipple 2 1/2 " | PCS | 4
31 | Union 2 1/2 " | PCS | 4
32 | PE adapter 63mm to 2" | PCS | 4
33 | Skilled labour on site | md | 0.5
Piping and fitting work of Network
34 | Pipe 90 mm HDPЕ 100: Pipe 90 mm OD, HDPЕ 100, РN-10, Thickness 5.4 mm & Weight 1.46 kg/m | m | 131
35 | Pipe 75mm HDPЕ 100: Pipe 75mm OD, HDPЕ 100, РN-10, Thickness 4.5 mm & Weight 1.02 kg/m | m | 674
36 | Pipe 63mm HDPЕ 100: Pipe 63mm OD, HDPЕ 100, РN-10, Thickness 3.8 mm & Weight 0.721kg/m | m | 167
37 | Pipe 50mm HDPЕ 100: Pipe 50mm OD, HDPЕ 100, РN-10, Thickness 3 mm & Weight 0.453kg/m | m | 186
38 | Pipe 40mm HDPЕ 100: Pipe 40mm OD, HDPЕ 100, РN-10, Thickness 2.4 mm & Weight 0.295kg/m | m | 2860
39 | Pipe 90 mm HDPЕ 100: Pipe 90 mm OD, HDPЕ 100, РN-16, Thickness 8.2 mm & Weight 2.14kg/m for well to Reservoir | m | 111
40 | PVC pipe 4" for covering of stand taps | m | 77
41 | Glass wool for the 100m length pipe 75@ with installation. | m | 100
42 | Pipe Fittings | lot | 1
43 | Skilled labor on site | md | 5.295
44 | Unskilled labor on site | md | 2.471
Solar System
45 | 2.5 inch Submersible pump in stainless steel. Stainless steel EN 1.4401 AISI 316, Rated power - P2: 5.5 kW, Rated voltage: 3 x 220-230 V Main frequency: 50 Hz Avg. water production per day: (12.31 m³/h) , Total dynamic head: 93.58 m , Pump Max head:121 m Solar pump 5.5 KW according to the technical specification and requirements, The contractor must submit a manufacturer warranty for the solar Pump for a period not less than 3 years. The visible label on a solar panel with technical specification and accepted by MRRD The contractor must submit all the required certificates for the solar pump The serial number of the Solar pump should be certified by the manufacturing company | No | 1
46 | Wire 16 mm2 for submerssible pump, | m | 100
47 | Renewable solar inverter with its Control box and Fuse box 3-phase 208V, 380V or 440V IP66-5.5KW 18A Quick Setup wizard preconfigured inputs Build in MPPT (Maximum Power Point Tracking) AC&DC power source compitible solar solution for up to 250kw and compitible with pump and whole required tools. Compitible inverter: IP 66 , pure sine wave ,VFD and soft starter Also with (SPD) surge protection Device As per needed in whole sytem and remote Monitoring data logging and remote controlling device Contractor must submit manufacturer warranty for inverter for a period not less than 3 years. Contarctor must submit all required certificates for inverter,and accepted by MRRD Serial number of inverter should be certified by manufacturing company . | No | 1
48 | Solar panels 8100 watt, standard: Range of ambient temperature: 233-358 K Electrical data: Maximum power point voltage: 30.9 V. to 31.2 V. Open circuit voltage: 37,7 V to 45.8 Max power point current: 8.42 A Module shortcut current: 8.89 A Maximum power output: 260 W to 270 W. Solar module type: POLYCRYSTALLINE CE certificate for monocrystalline and monocrystalline, ISO 9001:2007 Certificate, DIN EN certificate, Efficiency for Monocrystalline 18%-20%, Efficiency for Polycrystalline 15%-18%, Performance to 10 years (min 90% power output), Performance to 25 years (min 80% power output), Visible lable on solar panel with technical specification and accepted by MRRD.having certificate from manufacturer. | No | 8100
| Solar Panels Frames with stand for 30 Solar Panels. | No | 3
49 | electrical solar cable 1*10mm2 | m | 50
50 | electrical sensor cable 3*1.5mm2 | m | 100
51 | Maintenance box for inverter Switch | No | 1
52 | Plastic Rope | m | 200
53 | Cable locking Clip | No | 20
54 | Well Probe Sensor | No | 1
55 | Float Switch set (Mechanical Device for tank water level detection from well to reservoir with with cable and all other necessary tools) | No | 1
56 | earthing system | set | 1
57 | Delivery and Installation Cost | Lot | 0
Drilling of well
58 | Well drilling with percussion machine with 16" dia | m | 100
59 | Diameter=(8") inches, Class D, Min Wall Thickness (10.3 ) mm, Min weight (10.3 kg/m) According to ASTM D1785 Sch.80, DIN 8061, DIN 8062, ASTM F480 Standards. (the length of filter and casing should be declared after drill analysis and ground strata) | m | 60
60 | PVC Filter Pipe 8" dia Class D, opeing area does not exceed 25% of total area. | m | 40
61 | Gravel Packing back of the filters pipes in 25m length, based on soil texure, River Gravel sized from 3mm to 12mm according to the soil texture, as per advise of WVA WASH Engineer | m | 5.6
62 | Backfilling of Casing Pipe with soft Clay without any gravel | m3 | 3.74
63 | Pump Test for detemination of Hydrogeological parameters | Hour | 8
64 | Supplying and installation of all required fittings for well | Lot | 1
65 | Isogam one layer for the top of the water reservoir | m2 | 24.5
66 | Supply and istallation of metallic sign board | No | 2
67 | Metrering System: House connection from main pipe to inside houses, public buildings (school, mosque and clinic) with its all accessories including 1/2" Saddle clamp, Elbow, Female threaded adapter, (MTA), Gate valve, Water meter,Meter Box Non return valve, Water tap, Socket with 20m Pipe 20mm OD, HDPЕ 100, РN-20, Thickness 2.3 mm & Weight 0.133kg/m. as attached drawing | No | 110
Total Cost for Jar Qala Project |  |  |  |  | 0
This BoQ contains required in the Offer documents and shall be signed by a duly authorized person. Any addition, deletion or alteration in the BoQ may result in rejection of the Offer.Please have a Site visit before submit your offer and also attache the site visit picture with your bid documents
The works actually executed shall be measured, contractor shall visit the site of the works and obtain all information that may be necessary for completing their offer as under the provision of this contract no claim for additional work is accepted once the contract is signed.
Mobilization, Demobilization, Access road to construction site or other temporary works required for the execution of the items listed above, plus site restoration will be the responsibility of the contractor. Hence all the unit prices above are assumed to cover all activities associated with the works mentioned, and the total contract cost quoted is all inclusive to complete the total works.
Work Completion Certificate will provide after the measurement take place by WV team. The network scheme (length of the pipes) may change in field due to the commuity members request so the pipes will measure base on actual work completed in field with consideration of the quality of the work then the work completion certification will provide.
Prepared by: | Sayed Masoud Tural
Designation: | WASH Engineer
Signature:
Date: