## Taheri Haji Saleh BoQ for PR
WORLD VISION INTERNATIONAL DAWAM WASH Project BoQ for Solar Powered Water Supply Project
Village/CDC: Taheri Haji Saleh District: Dawlat Abad Province: Faryab
S/N | Activity/Item/Description | Unit | Quantity | Unit Cost AFN | Total Cost AFN | Remarks
A-(R.C.C Ground Water Tank+ Valve Box)
A1 | Site Preparation: Proposed Tank and Valve box site preparation according to technical specification and engineering considerations. | M2 | 40
A2 | Foundation Excavation: Proposed water Tank and Valve box foundation excavation, According to attached technical drawing, technical specification and engineering considerations. | M3 | 50
A3 | Back Filling : Back filling by well-compacted materials (the compaction should be layer by layer according to Engineering technical considerations. | M3 | 7
A4 | P.C.C (Plain Cement Concrete), M(1:2:4): in Water tank and Valve box , According to attached construction materials Specification with proper curing. | M3 | 3.5
A5 | R.C.C (Reinforced Cement Concrete), M-(1:1.5:3): R.C.C work including Bar-bending and Form working, According to attached drawing, Specification and engineering consideration with proper Curing. | M3 | 28
A6 | Water Stopper: Installation of Water Stopper according to drawing. | M | 22
A7 | Plastering Work (Interior of Water Tank) M(1:3): The plaster should have water proof admixture (ISOMAT) products according to technical requirements, with proper curing. | M2 | 85
A8 | Plastering Work (Exterior Side of Water Tank) M(1:3): The Materials Should be according to enginnering Specification( should be proper and clean). | M2 | 60
A9 | Painting work Painting work of water tank Weather Shield 100% with Office Logo. | M2 | 60
A10 | Roof Insulation: Supply and installation of Isogam weight 42 Kg and thickness 4mm | M2 | 22
A11 | Installation of Iron Gate. Installation of iron gate for tank manhole ( 3 mm Steel sheet) With its relevant features/fittings according to drawing. | M2 | 0.8
A12 | Interior Ladder of tank Supply and installation of ladder in interior side of the Water tank according to Attached Drawing Specification. | M | 2
A13 | Inlet GI Pipe. Supply and Installation Flanged GI Pipe Ø 3", Min Wall thickness =2.9 mm, Min Weight =6.25 Kg/M with Nut+bolt+Washer and other accessories. | M | 3
A14 | Over flow Pipe: Supply and Installation Flanged GI Pipe Ø 2 1/2", Min Wall thickness =2.9 mm, Min Weight =5.20 Kg/M with Nut+bolt+Washer and other accessories. | M | 3
A15 | Outlet Pipe : Supply and Installation Flanged GI Pipe Ø 3", Min Wall thickness =2.9 mm, Min Weight =6.25 Kg/M with Nut+bolt+Washer and other accessories. | M | 3
A16 | Covering Glass wool: covering the inlet and outlet pipe with glass wool and iron sheet (th=0.5mm) with all required activities according to technical requirements | Job | 1
A17 | Drain Out Pipe: Supply and Installation Flanged GI Pipe Ø 2", Min Wall thickness =2.6 mm, Min Weight =3.81 Kg/M with Nut+bolt+Washer and other accessories. | M | 3
A18 | Ventaliation Pipe: Supply and Installation GI Pipe Ø 2", Min Wall thickness =2.6mm, Min Weight =3.81Kg/M with 2 Elbows, and 1-Stad. | M | 1
A19 | PVC Rain Water Drain Pipe: Supply and Installation of PVC, class-C Pipe Ø 2", with all required activities and engineering considerations for roof rain water drinage. | M | 2
A20 | Flanged Gate Valve : Supply and installation of Flanged Gate Valve Ø 2" with Nut Bolt and Washers and other accessories. And with relevant composite fitting, should be connected with (OD-63 ) GI pipe, according to attached drawing. | No | 1
A21 | Flanged Gate Valve : Supply and installation of Flanged Gate Valve Ø 3" with Nut Bolt and Washers and other accessories. And with relevant composite fitting to be connected with network main pipe( OD 90) mm HDPE pipes, according to attached drawing | No | 1
Sub Total for Ground Tank and Valve Box |  |  |  |  | 0
Water Tank construciton should be according to attached drawing, Technical specifiation and Engineer recomendations, all concrete elements and other construciton process should be properly cured, the cosntruction materials (Sand, Gravel, Crushed Gravel, Portland Cement, Steel Bars and Pipe should be best quality and according to attached Specification).
B | BoQ for House connection StandPost./ Total # of Stand post 123
B1 | Excavation Work: Excavation of Each stand post foundation according to Designed drawing and Site conditions. | M3 | 856.08
B2 | Stone bolder Pitching: Supply and pitching of stone in foundation and surrounding area of stand post. | M3 | 34.7782
B3 | P.C.C (Plain Cement Concrete) M(1:2:4) The construction materials should be according to attached Specification. | M3 | 24
B4 | PVC Stand Pipe: Diameter=4", Class B, Min Wall thickness (3.4 mm), min Weigth=1.17 Kg/m | M | 123
B5 | Back Filling & Earth work: Back Filling , Cleaning, Drain out, Site preparation and soak pit according to site requirement. | M3 | 797.2
Sub Total Cost of Stand Posts |  |  |  |  | 0
The stand post should be prperly selected in houe considering all Hyginic recomendaitons, water management should be properly considered.
C | BoQ Well Boring and Development.
C1 | Site Preparation: Including leveling+Trimming and installation of Well drilling machine. | M2 | 10
C2 | Well Drilling by Percussion Machine: Diameter=(16") inches, The sampling should be recorded from each geological formations in proper sample box and Recording sheet. | M | 100 |  |  | Its Propsing depth, The actual depth will be depend to soil texture and geological strata.
C3 | Gravel Packing: the Size of Gravel Packing (3-6) mm, the exact size will be declared after boring and Well Hydralogical calculations, the Gravel should be clean and technical acceptable. | M3 | 8.5 |  |  | Depend on soil texture and geological starta
C4 | Soil/Clay : Supply and applying Clay soil for Blocking the Casing side of water well, special precausion should be considered. | M3 | 4.2 |  |  | Depend on soil texture and geological starta
C5 | Supply and Installation of PVC Casing and Filter Pipe: Diameter=(8") inches, Class D, Min Wall Thickness (10.3 ) mm, Min weight (10.3 kg/m) According to ASTM D1785 Sch.80, DIN 8061, DIN 8062, ASTM F480 Standards. (the length of filter and casing should be declared after drill analysis and ground strata) | M | 100 |  |  | the Extact Pipes Will be declared after well design
C6 | R.C.C for Well Protection Box Construction, M(1:1.5:3) RCC (M:1:1.5:3) for Well protection box including Varnished steel form working, bar bending and other requirements according to drawing and technical specification. | M3 | 1.4294
C7 | Installation of Iron Gate. Installation of iron gate for well protection box, including anti-rust painting and be lockable ( 4 mm Steel sheet) With its relevant features/fittings according to drawing. | M2 | 1.96
C8 | Supply and Installation of PVC fittings: Cable, Screw, Glue and other require materials. | L.s | 1
C9 | Well Cleaning : Cleaning should be carried out by compressor Machine. | Job | 1
C10 | Pump Test: Proper pump data should be recorded, the test should be min for 8 hours. | Job | 1
Sub-Total Cost for Well Construction |  |  |  |  | 0
Well drilling should be according to site condition and attached technical drawing and its specification, each geological formation and starta should be properly sampled in Well sample box and relevant technical sampling record book, depth determination should be with close consultation of WASH engineer, well cleaning shold be propely carried out, during pump test the relevant data should be properly recorded to assure well yield and future responding for community demands.
D | BoQ of Boundary Fencing for PV-System
D1 | Excavation in Foundation: Excavation according to drawing and technical requirements. | M3 | 25
D2 | Stone Masonry Work: Stone masonry for foundation and superstructure: use 1:4 ratio of mortar, stone shall have high bearing capacity and smooth surface for decoration. With it’s all related activities according to the drawing and technical specification | M3 | 32
D3 | Pointing Work Pointing of stone masonry with 1:4mortar of cement and sand with it’s all related activities according to required specification. | M2 | 70
D4 | P.C.C (Plain Cement concrete) M(1:2:4) According to Attached Drawing and its specification | M3 | 10.5
D5 | Fence Work : Supply and installation of GI-Pipes 2.5"(wall Th=2.9mm, weigth=6.25 kg/m) , GI-Net Mesh (wire dia=3mm) and Barbed wire with all required activities acoording to attached drawing, technical requirements and engineeeirng recommendations. | M | 67
D6 | Painting Work of Super Structure stone: Whether Shield Painting work (100%) with three coats. | M2 | 70
D7 | Gravel Filling: Supply and laying of gravel at boundry fencing area according to techncial requirements with 10cm thickness. | M3 | 28
Sub-Total Cost for boundary Fencing Construction |  |  |  |  | 0
E | BoQ for Gate Valve Box
E1 | Excavation Work: Excavation of Each Valve Box foundation according to Designed drawing and Site conditions. | M3 | 9
E2 | Stone Masonry Work: Stone masonry for foundation and superstructure: use 1:4 ratio of mortar, stone shall have high bearing capacity and smooth surface for decoration. With it’s all related activities according to the drawing and technical specification | M3 | 6.7
E3 | Flanged Gate Valve : Supply and installation of Flanged Gate Valve Ø 2" (PN-10) with Nut Bolt and Washers and other accessories. And with relevant composite fitting to be connected with network main pipe ( OD 63) mm HDPE pipes, according to attached drawing complete work. | No | 2
E4 | R.C.C for Gate valve Box Cover, M(1:1.5:3) R.C.C work for gate valve box inluding Varnished Form, Bar bending and other technical requirments. | M3 | 0.5
E5 | P.C.C (Plain Concrete and Cement)M(1:2:4) according to attached Drawing and technical specification | M3 | 1
E6 | Back Filling & Earth work: Back Filling , Cleaning the site according to site requirement. | M3 | 3
Sub Total Cost of Gate Valve Box |  |  |  |  | 0
Gate Valve Box construciton should be according to attached drawing, Technical specifiation and Engineer recomendations, all concrete elements and other construciton process should be properly cured, the cosntruction materials (Sand, Gravel, Crushed Gravel, Portland Cement, Steel Bars and Pipe should be best quality and according to attached Specification).
F | BoQ for Pipe networks
F1 | Excavation of Trench: Excavation of trench (Soft and Semi soft Soil) According attached Drawing and Specification. | M3 | 1222.24
F2 | Back Filling of Trench: Back Filling of trench with proper compaction, curring and caution according to attached drawing. | M3 | 916.68
F3 | Back Filling with Soft Soil: Back Filling of trench with proper compaction, curring and caution, | M3 | 305.56
F4 | House Connection System: House connection from main pipe to inside houses, public buildings (school, mosque and clinic) with its all accessories including 1/2" Saddle clamp, Elbow, Female threaded adapter, (MTA), Gate valve, Water meter, plastic meter box, Non return valve, Water tap, Socket with 20m Pipe 20mm OD, HDPЕ 100, РN-20, Thickness 2.3 mm & Weight 0.133kg/m. as attached drawing | No | 123
F5 | HDPE/Pipe/PN10/Dia=40mm (SDR17)- (W.T-2.4mm)- Weigth(0.295Kg/m), Comply ISO4427, DIN8074, ASTM D2239, ASTM D2737, ASTM D3035, ASTM D2515 All relevant marks should be attached in pipe (Bar, mesurment length, Standards). | M | 1980
F6 | HDPE/Pipe/PN10/Dia=50mm (SDR17)- (W.T-3mm)- Weigth(0.453Kg/m)ISO4427, DIN8074, ASTM D2239, ASTM D2737, ASTM D3035, ASTM D2515 All relevant marks should be attached in pipe (Bar, mesurment length, Standards). | M | 101
F7 | HDPE/Pipe/PN10/Dia=63mm (SDR17)- (W.T-3.8mm)- Weight(0.721Kg/m)ISO4427, DIN8074, ASTM D2239, ASTM D2737, ASTM D3035, ASTM D2516 All relevant marks should be attached in pipe (Bar, measurement length, Standards). | M | 314
F8 | HDPE/Pipe/PN10/Dia=75mm (SDR17)- (W.T-4.5mm)- Weigth(1.02Kg/m)ISO4427, , Comply ISO4427, DIN8074, ASTM D2239, ASTM D2737, ASTM D3035, ASTM D2515 All relevant marks should be attached in pipe (Bar, mesurment length, Standards). | M | 304
F9 | HDPE/Pipe/PN10/Dia=90mm (SDR17)- (W.T-5.4mm)- Weigth(1.46Kg/m)ISO4427, , Comply ISO4427, DIN8074, ASTM D2239, ASTM D2737, ASTM D3035, ASTM D2515 All relevant marks should be attached in pipe (Bar, mesurment length, Standards). | M | 496
F10 | PE Fittings 10 Bars: (Flanged adapter, GI-Flanged Valve in pipe network, Sockets, Elbows, TEEs, Saddle Clamps, Reducers, M/F Adapter and etc.) with Supplying and installation according to drawing and its specifications. | L.s | 1
F11 | Pipe Works (Plumbing): Supply, Installation, Laying and fitting of HDPE+GI pipes according to attached Drawing and its specification. | L.s | 1
Sub Total cost of Pipe network |  |  |  |  | 0
Selection of pipe alignment should be with close consultation of World Vision Afghanistan Technical engineer and attached drawing, The HDPE pipe should be tested in labartory according to MRRD requirment and the report should be submitted and varified by technical enigneer.
G | BoQ for Solar Panels
G1 | Excavation of Foundation: Site preparation and excavation in foundation for solar frame: | M3 | 2
G2 | Solar Panel: Providing and insatallation of Solar Panels according to MRRD Manual (European made or Equivelenat meet by IEC, ISO, TUV and CE, Solar array rated power = 8.1 KW Solar module type: POLYCRYSTALLINE or MONOCRYSTALLINE Water proof PV junction boxes IP68 for each array including DC Fuses, DC switch disconnectors, bus bars ,terminals, ducts or trays, supports & labels suitable to the PV arrays loads. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 years. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company, for more details and electrical parameters refer to attached Design. | Watt | 8100 |  |  | The # of Solar depend to Redesign of Pump PV system
G3 | Submersible pump with its Compatible inverter, control box and Fuse box in stainless steel. Eupean Made Technalogy Comply EN 1.4301 (AISI 304).EN 1.4301 (AISI 304). EN 1.4539 (AISI 904L). EN 1.4401 (AISI 316).. Rated power - P1- 5.852Kw , P2-5.5KW Rated voltage: 3*220-230 V Main frequency: 50 Hz Compatible inverter:RSI 3x208-240V IP66 7.5kW 31A, Pure sine wave, VFD and soft starter Avg. water production per day: (99.3 m³/day), Total Dynamic Head is considered = 124.1 m. it is inital Assumed head the final will be declare after bore well and pump test. distance between tank and well =838 M. Solar pump P2- 5.5 KW according to the technical specification and requirement, Contractor must submit manufacturer warranty for solar Pump for a period not less than 2 years. Contractor must submit all the required certificates for solar pump Serial number of Solar pump should be certified by manufacturing company | set | 1 |  |  | the Pump Model Depend to Redesign of the system.
G4 | Well Probe Sensor: Dry running sensor including Electrical Wire and other fittings , According to Attached Electrical parameters | set | 1
G5 | Motor (Sumbersible drop Cable) 12 mm² 3-phase cable for power and 1-phase cable for ground according to drawing and technical requirements. | M | 120
G6 | PV System-Inverter Cable (1x12mm2), Cable from PV-combiner Box to Inverter | M | 20
G7 | Grounding/Earthing. All system Should be proper Grounded by ground Rod and Copper Cable (PV, PV-Frame, Inverter, Sumersible and other electrical installed features) | LS | 1
G8 | Pump Holding Rope : Plastic made, diameter=16 mm Double line with its relevant accessoires and features. | M | 220
G9 | Electrical Conduite: Electrical Conduite for External Wire: | L.s | 1
G10 | Circuite Breaker and Auto Fueses: Circuite Breaker and Auto fueses should be installed to prevent system during electrical issues. | Set | 1
G11 | HDPE/Pipe/PN16/Dia=90mm (SDR17)- (W.T-8.2mm)- Weigth(2.12Kg/m)ISO4427, , Comply ISO4427, DIN8074, ASTM D2239, ASTM D2737, ASTM D3035, ASTM D2515 All relevant marks should be attached in pipe (Bar, mesurment length, Standards). | M | 910
G12 | PE and GI Fittings: PE and GI 16 Bars fittings for Sumbersible-Tank (PE Flanged Adapter, Flanged Elbow, Flanged Sockets and etc.) according ot technical requirment and site conditions. | L.s | 1
G13 | Boulder Stone Pitching: Bolder Stone pitching in foundation of Solar system frame according to drawing and technical requirements | M3 | 1
G14 | P.C.C (Plain Concrete and Cement)M(1:2:4) according to attached Drawing and technical specification | M3 | 1
G15 | RCC (Reinforced Concrete and Cement)-(M:250) for Solar Stand: including Varnished steel form working, bar bending and other requirements according to drawing and technical specification. | M3 | 3
G16 | PV-Solar Frame for Solar Panels: Supply and installation of Stand and frame for solar panels, able to be rotated manually ( Steel pipe dia 6", th=4mm, Profile box 40 x 80, th=2mm) | Frame | 3
G17 | Back Filling and Compaction: Back Filling, Draining out, and Site Cleaning of Solar system plant. | M3 | 2
G18 | Sign Board: Supply and istallation of metallic sign board. | No | 1
Sub Total cost of Pipe network |  |  |  |  | 0
Attached is the solar system Design, The Solar pump PV system has designed based on technical survey, the actual design well be determined after boring well to show well discharge, dynamic water table, draw down and etc. the contractor will be paid based on actual works. - Construction site Must be cleaned Properly after construction Work is completed.
Grand Total for All BoQ (A+B+C+D+E+F+G) |  |  |  |  | 0
Prepared by: Sayed Masoud Tural
Designation: WASH Engineer
Signature:
Date: