## Detail BoQ
INTERNATIONAL MEDICAL CORPS
PROGRAM DEPARTMENT/WASH UNIT
Bill of Quantity for Rehabilitation of Solar powered water supply network
Project Name: Rehabilitation of Water Supply Network Province : Ningarhar District: Khogyanai Village: Chamtala Block-24
S/N | Activity/Item/Description | Unit | Quantity | Unit Cost AFN | Total Cost AFN | Remarks
A | BoQ for Well Development.
A.9 | Pump Test: Proper pump test data should be recorded, the test should be min for 8 hours. | Job | 1 |  | 0
Sub total for pump test of existing well |  |  |  |  | 0
B | BoQ For rehabilitation of the Existing Elevated Tank
B.1 | painting Plastic Wheather Sheet رنگمالی با رنگ پلاستیکی | M2 | 190 |  | 0
B.2 | Supply and installation of Galvanized Iron pipe for the inlet of purposed net work, Internal dia.3" پايپ آهني ملمع جستی بقطر داخلي | m | 15 |  | 0 | Inlet pipe of elevated tank
B.3 | Supply and installation of Galvanized Iron pipe for the inlet of purposed net work, Internal dia.4" پايپ آهني ملمع جستی بقطر داخلي | m | 13 |  | 0 | Outlet pipe of elevated tank
B.4 | Supply and installation of Galvanized Iron Socket, diameter 3"سامي آهني ملمع جست بقطر | NO | 2 |  | 0
B.5 | Supply and installation of Galvanized Iron Nipple, diameter 3"اشتت آهني ملمع جست بقطر | NO | 2 |  | 0
B.6 | Supply and installation of Galvanized Iron Union 3" پیوند آهني ملمع جستی بقطر | NO | 2 |  | 0
B.7 | Supply and installaiton of FlangeAdapter Size (90x3") اداپتر نوع پولی ایتیلین به سایز | NO | 1 |  | 0
B.8 | Supply and installation of Galvanized Iron Elbow 3" diaزانو خم آهني ملمع جستی بقطر | NO | 2 |  | 0
B.9 | Supply and installation of Galvanized Iron Elbow 4" diaزانو خم آهني ملمع جستی بقطر | NO | 2 |  | 0
Sub total of rehabilitation of Existing Elevated Tank |  |  |  |  | 0
C | BoQ For Solar Pump System
C.1 | Supply and installation of Grundfos (SP 18-13), Motor AC DRIVE SUB 6" 7.5 kW Pump,11KW compitable inverter ,with compitable Controller , with out let size 2.5 In), or Equivalent according to MRRD registered list of companies & Specification (the manufacturer company should not be restricted with IMC) Avg. water production per day: 144 m3/day, flow rate of 18m3/hr, Total head: 89.5m Solar pump 7.5 KW according to the technical specification and requirement, سولر پمپ 7.5 کیلوات معه 11 کیلو وات انورتر ،کنترول باکس وفیوز باکس از کمبنی لورنز ویا معادل آن طبق مشخصات داده شده Contractor must submit manufacturer warranty for solar Pump for a period not less than 3 years. Contractor must submit all the required certificates for solar pump Serial number of Solar pump should be certified by manufacturing company | No | 1 |  | 0 | ظرفیت آب دهی پمپ = 144m3/day باشد و در صورت پایین آمدن سطح آب پمپ بشکل اتوماتیک خاموش شود.
C.2 | Solar panels(540)watt, or Equivalent according to MRRD registered list of companies & Specification (the manufacturer company should not be restricted with IMC) Solar module type: POLYCRYSTALLINE or MONOCRYSTALLINE PV module used in solar power plant/system must be warranted for 10 years for their material, manufacturing defects, workmanship. The output peak watt capacity which should not be less than 90% at the end of 10 years and 80% at the end of 25 years. | watt | 10920 |  | 0
C.3 | Well Probe V2 (Well probe sensor V2), Mechanical float switch for dry run protection of solar pumps, Cable splice kit 2.5-6mm2,Safty rope for holding of solar pump, Ground rod with Cooper Cable, conduit pipe,Wire tire and etc , complete work with related accessories. | LS | 1 |  | 0
C.4 | Drop cable, RD TML-B 2x1.5mm2 Cable for dry running protection, | m | 70 |  | 0
C.5 | extention and rehabioitation of Solar panels stand steel,25 and 45 deg, Large (panels suport structure) size of current of solar stand is (5.5mX4.1m) ترمیم و انکشاف پایه سولر پینل ها ابعاد فرم موجوده 5.5 متر در 4.1 متر میباشد. | set | 1 |  | 0
C.6 | Submercible drop cable (4*6)mm2 from Controlar to solar pump کیبل برق از کنترولر الی پمپ | m | 40 |  | 0
C.7 | Cable (2*1.5)mm2 کیبل برق | m | 70 |  | 0
C.8 | Cable (1*10)mm2 کیبل برق | m | 32 |  | 0
C.9 | Supply and installation of solar pump set and solar panels انتقال ومونتاژ سبمرسیبل پمپ و سیستم سولر پنیل ها | set | 1 |  | 0
Sub-Total Cost for Solar Pump System (USD) |  |  |  |  | 0
D | BoQ for Rehabilitation of well protection Box
D.1 | Plaster work with cement-sand, M: 1:3 پلسترکاری با مارک مخلوط سمنت وریگ مارک مصاله | m2 | 7 |  | 0
D.2 | Prevision and installation of Iron sheet Cover with 3mm thick according to design with all required activities | LM | 1 |  | 0
D.3 | Prevision & installation of Well Cap made of 3mm thick Iron sheet according to design with all required activities | LM | 1 |  | 0
D.4 | Supply & installation of Flanged None Returning Valve Nominal diameter 3'' (good quality) with all accessories according to design & all required activities | NO | 1 |  | 0
D.5 | Supply & Installation of Flanged Flow Meter3'' with all accessories according to design & all required activities. | NO | 1 |  | 0
D.6 | Supply and installation of Galvanized Iron Socket, diameter 3"سامي آهني ملمع جست بقطر | NO | 4 |  | 0
D.7 | Supply and installation of Galvanized Iron Nipple, diameter 3"اشتت آهني ملمع جست بقطر | NO | 4 |  | 0
D.8 | Suuply and installation of High Density Polyethylene 90mm Elbow with all accessories. | NO | 1 |  | 0
Sub-Total Cost for rehabilitation of well protection (Afs) |  |  |  |  | 0
E | BoQ for Construction of Gate Valve & Flow Meter Box
E.1 | Excavation of foundation in ground type 3-4 کندن کاری درزمین قسم سوم وچهارم | m3 | 4.32 |  | 0
E.2 | Back filling with Gravel under the PCC.پرکاری توسط جغل دریائی زیرکانکریت بدون سیخ | m3 | 0.323 |  | 0
E.3 | Plain Cement Concrete (PCC),for well head leveling according to the drawing M150 kg/cm2 (1:2:4) ۱:۲:۴ کانکریت بدون سیخ برای لیول کاری فرش با مارک مخلوط | m3 | 0.413 |  | 0
E.4 | Kilned brick masonry with mortar 1:4 (cement - sand) . خشت کاری پخته به مخلوط مساله (ریګ: سمنت) 1:4 | m3 | 1.76 |  | 0
E.5 | Plaster work with cement +sand, (1:3) پلستر کاری داخلی با مخلوط مساله با نسبت | m2 | 1.85 |  | 0
E.6 | Prevision & installation of sliding cover gate made of 3mm thick Iron sheet with all accessories according to design & all required activities | No | 1 |  | 0
E.7 | Back filling with Excavated materials | m3 | 1.44 |  | 0
E.8 | Supply & Installation of Flanged Flow Meter 4'' with all accessories according to design & all required activities | NO | 2 |  | 0
E.9 | Supply & Installation of Flanged Gate Valve 4'' with all accessories according to design & all required activities | NO | 2 |  | 0
E.10 | Supply and installation of sleev for crossing of pipe from wall of Gate Valve & flow meter box. | NO | 2 |  | 0
E.11 | Supply and installation of Galvanized Iron Socket, diameter 4"سامي آهني ملمع جست بقطر | NO | 4 |  | 0
E.12 | Supply and installation of Galvanized Iron Nipple, diameter 4"اشتت آهني ملمع جست بقطر | NO | 4 |  | 0
Number of Gate Valve and Flow meter Box |  | 1
Sub-Total Cost for Construction of G.V & Flow Meter Box |  |  |  |  | 0
F | BoQ for Construction of Gate Valve Box
F.1 | Excavation of foundation in ground type 3-4 کندن کاری درزمین قسم سوم وچهارم | m3 | 2.25 |  | 0
F.2 | Back filling with Gravel under the PCC.پرکاری توسط جغل دریائی زیرکانکریت بدون سیخ | m3 | 0.225 |  | 0
F.3 | Plain Cement Concrete (PCC),for well head leveling according to the drawing M150 kg/cm2 (1:2:4) ۱:۲:۴ کانکریت بدون سیخ برای لیول کاری فرش سرپوش چاه با مارک مخلوط | m3 | 0.12 |  | 0
F.4 | Kilned brick masonry with mortar 1:4 (cement - sand) . خشت کاری پخته به مخلوط مساله (ریګ: سمنت) 1:4 | m3 | 1.06 |  | 0
F.5 | Plaster work with cement +sand, (1:3) پلستر کاری داخلی با مخلوط مساله با نسبت | m2 | 4 |  | 0
F.6 | RCC Precast Slab (110*110*12 ) cm پریکاست سلب | PCs | 1 |  | 0
F.7 | Steal Cover Guidance for Cover opening & Closing of Gate valve | No | 1 |  | 0
F.8 | Back filling with Excavated materials | m3 | 0.56 |  | 0
F.9 | Supply and installation of sleev for crossing of pipe from wall of Gate Valve box. | NO | 2 |  | 0
Sub-Total Cost for Construction of 1 Gate Valve Box |  |  |  |  | 0
| No Gate Valve Boxes = | 7
Sub-Total Cost for Construction of 7 Gate Valve Boxes |  |  |  |  | 0
G | BoQ for Rehabilitation of 10 existing stand taps & Construction of Soak pit for existing stand post
G.1 | پلسترکاری مطابق نقشه با مارک 1:3 مصالحهPlaster work with cement-sand, M: 1:3 | m2 | 57 |  | 0
G.2 | کندنکاری برای ساختمان چاه جذب آب درسوم Excavation for Soakpit ground type 3 | m3 | 10 |  | 0
G.3 | پرکاری جغل Gravel filling | m3 | 10 |  | 0
G.4 | Supply & installation of all accessories of public stand post including 3/4" GI pipe ,Socket,Niple, Elbow, best quality nickel water tap complete work with related accessories. انتقال و منتاژپایپ جستی به قطر ۳/۴انچ ، ساکت،سامی،شتت.زانوخم ، شیردهن نکلی باتمام امور ایجابی آن | job | 10 |  | 0
SubTotal cost for rehabilitation of 10 Existing Stand Taps & Soak pit (USD) قیمت مجموعی برای ساختمان 10 عدد شیردهن |  |  |  |  | 0
H | BoQ for construction stand tap & Soak pit
H.1 | کندنکاری برای ساختمان شیردهن ها درسوم Excavation for Stand Tap ground type 3 | m3 | 10.9529 |  | 0
H.2 | کندنکاری برای ساختمان چاه جذب آب درسوم Excavation for Soakpit ground type 3 | m3 | 21 |  | 0
H.3 | پرکاری جغل Gravel filling | m3 | 26.6903 |  | 0
H.4 | کانکریت سیخدار مع قالب بندی با مارک 1:1.5:3 Reinforced Cement Concrete M: 1:1.5:3 with shuttering | m3 | 10.5 |  | 0
H.5 | کانکریت بدون سیخ به مارک Plain Cement Concrete M: 1:2:4 | m3 | 4.2 |  | 0
H.6 | پلسترکاری مطابق نقشه با مارک 1:3 مصالحهPlaster work with cement-sand, M: 1:3 | m2 | 119.6176 |  | 0
H.7 | Supply & installation of all accessories of public stand post including 3/4" GI pipe ,Socket,Niple, Elbow, best quality nickel water tap complete work with related accessories. انتقال و منتاژپایپ جستی به قطر ۳/۴انچ ، ساکت،سامی،شتت.زانوخم ، شیردهن نکلی باتمام امور ایجابی آن | job | 21 |  | 0
SubTotal cost for 21 No Stand Taps & Soak pit (USD) قیمت مجموعی برای ساختمان 21 عدد شیردهن |  |  |  |  | 0
I | BoQ for Distribution line (From Reservoir to Stand taps)
I.1 | Excavation of pipe trench for distribution pipes laying in ground type 4,3 کندن کاری درزمین قسم | m3 | 1422 |  | 0
I.2 | Back filling of pipe trench by excavated material.پرکاری خاک معه تپک کاری | m3 | 995 |  | 0
I.3 | Back filling of pipe trench by soft soil material.پرکاری خاک میده معه تپک کاری | m3 | 427 |  | 0
I.4 | Supply and laying of warning tap according to the drawing | m | 2843 |  | 0
I.5 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 16 SDR 11), Outside Diameter: 32mm, wall thickness 3 mm ,weight 0.27kg/m, Best quality.پایپ پولی ایتیلین بقطر خارجی 32 ملی با فشارقابل برداشت 16 بار | m | 268 |  | 0
I.6 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness 2.4 mm ,weight 0.29kg/m, Best quality.پایپ پولی ایتیلین بقطر خارجی 40 ملی با فشارقابل برداشت 10 بار | m | 1867 |  | 0
I.7 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness 3 mm ,weight 0.45kg/m, Best quality.پایپ پولی ایتیلین بقطر خارجی 50 ملی با فشارقابل برداشت 10 بار | m | 263 |  | 0
I.8 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness 3.8 mm ,weight 0.72 kg/m, Best quality.پایپ پولی ایتیلین بقطر خارجی 63 ملی با فشارقابل برداشت 10 بار | m | 285 |  | 0
I.9 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 75 mm, wall thickness 4.5 mm ,weight 1.01kg/m, Best quality.پایپ پولی ایتیلین بقطر خارجی 75 ملی با فشارقابل برداشت 10 بار | m | 105 |  | 0
I.10 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 16 SDR 11), Outside Diameter: 90 mm, wall thickness 8.2 mm ,weight 2.14kg/m, Best quality.پایپ پولی ایتیلین بقطر خارجی 90 ملی با فشارقابل برداشت 16 بار | m | 85 |  | 0
I.11 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 110 mm, wall thickness 6.6 mm ,weight 2.15kg/m, Best quality.پایپ پولی ایتیلین بقطر خارجی 110 ملی با فشارقابل برداشت 10 بار | m | 40 |  | 0
I.12 | Supply and installation of Polyethylene Straight reducer,diameter (75x50) mmوصل کننده مستقیم نوع پولی ایتیلین | NO | 1 |  | 0
I.13 | Supply and installation of Polyethylene Straight reducer,diameter (63x50) mmوصل کننده مستقیم نوع پولی ایتیلین | NO | 1 |  | 0
I.14 | Supply and installation of Polyethylene Straight reducer,diameter (50x40) mmوصل کننده مستقیم نوع پولی ایتیلین | NO | 1 |  | 0
I.15 | Supply and installation of Polyethylene Straight Coupler, diameter (40x40) mmوصل کننده مستقیم نوع پولی ایتیلین | No | 1 |  | 0
I.16 | Supply and installation of Polyethylene Tee, Size (75x63x75)mmسه دهن نوع پولی ایتیلین | No | 2 |  | 0
I.17 | Supply and installation of Polyethylene Tee, Size (75x50x75)mmسه دهن نوع پولی ایتیلین | No | 1 |  | 0
I.18 | Supply and installation of Polyethylene Tee, Size (63x40x63)mmسه دهن نوع پولی ایتیلین | No | 5 |  | 0
I.19 | Supply and installation of Polyethylene Tee, Size (40x32x40)mmسه دهن نوع پولی ایتیلین | No | 28 |  | 0
I.20 | Supply and installation of Gate valve (good quality) Nominal Diameter = 2 1/2" best qualityگیت وال به قطر | No | 2 |  | 0
I.21 | Supply and installation of Gate valve (good quality) Nominal Diameter = 2" best qualityگیت وال به قطر | No | 4 |  | 0
I.22 | Supply and installation of Gate valve (good quality) Nominal Diameter = 1 1/2" best qualityگیت وال به قطر | No | 2 |  | 0
I.23 | Supply and installation of Gate valve (good quality) Nominal Diameter = 1 1/4" best qualityگیت وال به قطر | NO | 6 |  | 0
I.24 | Supply and installation of Galvanized Iron Nipple, diameter 2 1/2"اشتت آهني ملمع جست بقطر | NO | 4 |  | 0
I.25 | Supply and installation of Galvanized Iron Nipple, diameter 2"اشتت آهني ملمع جست بقطر | NO | 8 |  | 0
I.26 | Supply and installation of Galvanized Iron Nipple, diameter 1 1/2"اشتت آهني ملمع جست بقطر | NO | 4 |  | 0
I.27 | Supply and installation of Galvanized Iron Nipple, diameter 1 1/4"اشتت آهني ملمع جست بقطر | No | 12 |  | 0
I.28 | Supply and installation of End cup for the pipe 40mm فلق برای پایپ | NO | 12 |  | 0
I.29 | Sign Board for visibility of the project & messages لوحه برای پروژه | NO | 1 |  | 0
I.30 | Site preparation and clearance | LS | 1 |  | 0
Sub-Total Cost for distribution line (Afs.) |  |  |  |  | 0
Selection of pipe alignment should be with close consultation of IMC/Technical engineer and attached drawing, The HDPE pipe should be tested in laboratory according to MRRD requirement and the report should be submitted and verified by IMC/technical engineer.
Grand Total for All BoQ (A+B+C+D+E+F+G+H+I) |  |  |  |  | 0