## BoQ and Cost
Bill of Quantity for Construction of Kabotar Ghal Village's water supply Network
| Provice : Herat | Project : WoBs
| District : Kushk Robat Sangi | Sector : WASH
Village : Kabotar Ghal
No | Discriptions تشریحا ت | Unit واحد | Quantity مقدار | Cost/Unit (AFN) قیمت فی واحد | Total Cost (AFN) قیمت مجموعی | Remarks ملاحظات
BoQ for (Well)
1 | Digging of well based on drawing ( dia. 2.64m) | m3 | 109.422
2 | Supply and running cost of water pump for drying of water during the well digging | L.s | 1
3 | RCC ring(inside dia : 200cm, outside dia : 224cm, hight 50cm) | No | 40
4 | RCC Slab(Dia=2.24m thickness 12cm ) | m3 | 0.473
5 | Gravel Packing from sorted gravel round washed gravel the size of gravel should be determind after well drilling accordding to the sample of starta. | m3 | 25.74
6 | Back filling for Ring should be clay soil (mud) without gravel stone | m3 | 4.9
7 | Prepareing the technical report of well drilling, preparing well strata technical data table and making design of well according to the taken strata ( Location of Filter, Cassing and pump instalation depth ). | Ls | 1
8 | Pump test for determination of discharge of well and taking sample of water for quality test after water cleaning Under supervission of PRRD representative. . | hour | 8
Sub-Total Cost for ‌Well (AFN)
Note: The well will be manually excavated to a planned depth of 20 meters, with a static water level anticipated at 8 meters in the area. The physical test parameters have been verified and approved by the PRRD representative during the project's survey stage. No further activities, such as the procurement of solar pumps and panels, construction of the reservoir, or the pipe network installation, should proceed until the successful completion of the water quality test and pump test. The minimum required water flow rate for the well is 1.45 liters per second. Should the flow rate during the pump test fall below this threshold, the CARE WASH department reserves the right to either adjust the project's specifications or cancel subsequent activities.
BoQ for Solar pump system to Reservoir
1 | Supply and installation of Submersible Water Pump European-made, or its equivalent IP(65-68) 4SR6/13 2HP 1.5Kw 220V, with min 2 years warranty Avg. water production per day: (6m³/h) 48m³/day, Total head: 45m Solar pump 1.5 KW according to the technical specification and requirement Contractor must submit manufacturer warranty for pump for a period not less than 2 years. Contractor must submit all the required certificates for solar pump Serial number of Solar pump should be certified by manufacturing company and the pump should be MRRD Approved brands | No | 1
2 | Inverter(Hybrid) IP(65-68), 1.5kW 2 HP 220V with water proof metalic box and proper lock, The production company confirmation and all certificates are required, low noise, Support over-voltage, phase loss, Built-in start-stop button, operation easily.The invertor should provide required power from solar panels to the pump and run the system smoothly. MRRD preferred brands | NO | 1
3 | Supply and installation of solar panels internationaly certified by IEC, ISO, TUV and CE, Geran cells (455watt) Solar module type: POLYCRYSTALLINE or MONOCRYSTALLINE Water proof PV junction boxes IP68 for each array including DC Fuses, DC switch disconnectors, bus bars ,terminals, ducts or trays, supports & labels suitable to the PV arrays loads. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 years. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company and MRRD Approved brands | watt | 2730
4 | Stand for solar panels, able to be rotated manually, Footing (1*1*2)m based on drawing with color, stand should be coated with anti-rust and high-quality color according to CARE engineer's advice. | set | 1
5 | Well probe sensor high quality | set | 1
6 | Cable splice kit 2.5-6mm2 | set | 1
7 | Earthing system, standard type as a safety measure from lightening arrestor to protect human life as well as equipment. | m | 1
8 | Submersible pump drop cable from inverter to pump (4*2.5)mm2 | m | 60
9 | Safety rope for holding of solar pump with 12mm dia | m | 30
10 | Float switch ( Mechanically Activated Device for water level detection) high quality | No | 1
11 | Cable (2*4)mm2 | m | 35
12 | Electric conduit pipe for external power cables. | m | 45
13 | Cable (3*1.5)mm2 | m | 200
14 | Delivery and Installation Cost | set | 1
15 | Supply and installation for pipe paddle flange diameter 4'' (clip on the top of the well to hold up the riser main pipe) | No | 1
16 | Supply and installation of all fitting for connection system from well to reservoir | Ls | 1
Sub-Total Cost for Solar panels and solar pump(AFN)
BoQ for Boundary wall of solar panels
1 | Excavation in different ground types 3 | m3 | 13.2
2 | Stone masonry with cement- sand mortar M:1:5 | m3 | 19
3 | Plain Cement Concrete (PCC), M150 kg/cm2 (1:2:4) | m3 | 2.92
4 | Gravelling inside of boundary wall (Crush gravel) | m3 | 6
5 | Brick masonry with mortar 1:4 (cement - sand) | m3 | 13.06
6 | Plaster work with cement-sand inside and outside boundary wall | m2 | 244.8
7 | Painting of wall inside and outside | m2 | 244.8
8 | Pointing for out side and inside of Boundry wall with mortar 1:3 (cement -sand). M: 1:3 | m2 | 28
9 | Supply and installation of metallic gate by 20 Gauge GI iron sheet with lock | m2 | 2.29
10 | Supply and installation of Concertina wire on boundary wall of solar panel (complete) according to the drawing | m | 44
Sub-Total Cost for Boundary wall of solar panels (AFN)
BoQ for 10m3 (10000 lit) Reservoirs
1 | Excavation for reservoir in ground all type of soil. | m3 | 16.5
2 | Back filling with soil and excavated material . | m3 | 3
3 | Plain Cement Concrete (PCC), M150.(1:2:4) | m3 | 1.2
4 | Reinforced Cement Concrete (RCC), M200 including steel bars and shuttering according to the drawings. | m3 | 10
5 | Plaster work with cement-sand + padlow powder M: 1:3 for inside. M: 1:3. | m2 | 26
6 | Plaster work with cement-sand M: 1:3 for exterioir wall.M: 1:3 | m2 | 20
7 | Isogam insulation on roof of reservoir. | m2 | 8
8 | Supply and installation of iron gate for reservoir manhole (iron 3mm thick) and lockable frame with all required activities and as per drawing. | No | 1
9 | Supply and installation of 1 1/2" inch Galvanised Iron Ladder for reservoir with all required activites according to drawings. | No | 1
10 | Supply and installation of Galvanized Iron pipe for the inlet and out let pipe Internal dia.2" | m | 6
11 | Supply and installation of Galvanized Iron pipe for the over folw & washout pipe Internal dia.1 1/2" | m | 6
12 | Supply and installation of Flanged Gate valve Nominal Diameter = 2" with two flange adapter including all necessary to complete this job | No | 1
13 | Supply and installation of Flanged Gate valve Nominal Diameter = 1 1/2" with two flange adapter including all necessary to complete this job | No | 1
Sub-Total Cost for 1 No 10m3 (10000 lit) Reservoirs (AFN)
BoQ for Valve Box
1 | Excavation for reservoir in ground all type of soil. | m3 | 3.74
2 | Compacted earth with boulder | m3 | 0.576
3 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. | m3 | 1.77
4 | Plaster work with cement-sand, inside M: 1:3. | m2 | 5.12
Sub-Total Cost for 3 No valve box (AFN)
BoQ for River Crossing
1 | Excavation of pipe trench for river crossing pipes laying in ground type 3 according to the drawing | m3 | 127
2 | Back filling of pipe trench by excavated material. | m3 | 127
3 | Supplying, installation, laying and fitting in place of GI pipe 1 1/4" for 32mm HDPE pipe | m | 110
4 | Supplying, installation, laying and fitting in place of GI pipe 2 1/2" for 63mm HDPE pipe | m | 18
5 | Plain Cement Concrete (PCC), M150.(1:2:4) around GI pipe in river | m3 | 15.36
Sub-Total Cost for river crossing ( AFN)
BoQ for Distribution line (From Reservoir to House connection)
1 | Excavation of pipe trench for distribution pipes laying in ground type 3 | m3 | 1304
2 | Back filling of pipe trench by excavated material. | m3 | 1304
3 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 16 SDR 11), Outside Diameter: 32 mm, wall thickness 3 mm ,weight 0.278kg/m, Best quality. | m | 954
4 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness 2.4 mm ,weight 0.29kg/m, Best quality. | m | 658
5 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness 3 mm ,weight 0.45kg/m, Best quality. | m | 96
6 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness 3.8 mm ,weight 0.72 kg/m, Best quality. | m | 772
7 | Supplying and installation of all required fittings for well | LS | 1
8 | Supply and installation of Flanged Gate valve Nominal Diameter =2 " with two flange adapter including all necessary to complete this job | No | 1
9 | Supply and installation of Flanged Gate valve Nominal Diameter = 1 1/2 " with two flange adapter including all necessary to complete this job | No | 1
10 | Supply and installation of Flanged Gate valve Nominal Diameter = 1 1/4 " with fitting including all necessary to complete this job | No | 1
11 | House connection from main pipe to inside houses, public buildings (school, mosque and clinic) with its all accessories including 1/2" Saddle clamp, Elbow, Female threaded adapter, (MTA), Gate valve, Water meter, Non return valve, Water tap, Socket, 20mm HDPE pipe each and perfabricated heavy duty water meter box. | No | 60
Sub-Total Cost for distribution line (AFN)
BoQ for Misceillaneous Works:
1 | Misceillaneous Works | Ls | 1
2 | Delivery and Installation Cost | Ls | 1
3 | Supply and installation of metallic sign board with (50*50*50)cm foundation | No | 1
Sub-Total Cost for Misceillaneous Works (AFN
Total Cost AFN