## Zangi Saba
NCA, Afghanistan
احجام کارومواد مصرفی برای سیستم آبرسانی پایپ سکیم توسط سولر پمپ همرای آبرسانی قریه زنګی صبا ولسوالی غوریان ولایت هرات
Bill of Quantity for Zangi Saba Community solarized water supply system.
S/NO شماره | Discriptions تشریحا ت | Unit واحد | Quantity مقدار | Cost/Unit (AFN.) قیمت فی واحد | Total Cost (AFN.) قیمت مجموعی | Remarks ملاحظات
BoQ for New Bore well
1 | Well drilling with percussion (cable tool) machine diameter (12") depends on soil texture and Collecting sample of each Geological formation. برمه کاری چاه توسط میتود کوبه ای (کیبلی) به قطر(12 انچ) در هر نوع طبقات وهمچنان جمع آوری نمونه طبقات جیولوجیکی | m | 60 |  | 0
2 | Transportation and Installation of PVC casing pipe class -D, dia. 8", wall thickness (10.3 - 11.9)mm ,weight 10.05 kg/m, BSS 3505/3506 , ASTM 1785-94, including 20cm for each pipe connection which wont be counted. all the necesseries are included like, Glue, Screw, centrelizer and rope. (PVC quality Lab test result is required). the PVC casing should be installed at the right middle of the borehole and the end cap should also be installed. noreover, filter pipes should be as per the soil texture also the filter pipes should only installed at the parts of aquifers تهیه ونصب کیسنگ پی وی سی کلاس دی به قطر 8 انچ | m | 25 |  | 0
3 | Supply and installation of Filter pipe PVC Class-D, dia. 8", wall thickness (10.3 - 11.9)mm ,weight 10.05 kg/m, BSS 3505/3506 , ASTM 1785-94. Total area for filter pipe openings should not be more than 25% of total area. all the necesseries are included like, Glue, Screw, centrelizer and rope (PVC quality lab test result is required). the PVC casing should be installed at the right middle of the borehole. تهیه ونصب فلترپی وی سی ازنوع کلاس دی قطر 8 انچ فیصدی مساحت مسامات فلتر از25 فیصد مساحت مجموعی تجاوز نکند | m | 36 |  | 0
4 | Gravel Packing from sorted gravel round washed gravel the size of gravel should be determind after well drilling accordding to the sample of starta depends on soil texture (casing pipe and filter). اندازه قطر جغل در اطراف پایپ فلتر و کیسینگ نظر به ترکیب طبقات در نظرگرفته شود اگر طبقات مقابل فلتر از ذرات میده دانه باشد اندازه قطر جغل 3 الی 6 ملی متر و اگر از ذرات بزرگ دانه باشد اندازه قطر جغل 5 الی 10 الی 12 ملی متر جغل لشم دریائی و شسته باشد یا پرکاری جغل دراطراف پایپ فلتر ازنوع سورت شده بوده جغل مدور لشم دریائی وشسته که اندازه دانه های جغل نظر به ترکیب طبقات بعد از حفاری تعین میگردد.. | m3 | 2.4 |  | 0
5 | پرکاری عقب کیسنگ ازخاک بدون ریگ وجغل باشد. Back filling for casing pipe should be clay soil without gravel stone | m3 | 1.5 |  | 0
6 | Pumping test with submersible pump for specifying hydro-geological parameters and water discharging rate of well. Pumping test includes finding the discharge of well, dynamic water level, static water level, drawdown, pump installation depth, and recharge time, and all the necessary equipment should be available during pumping test. ex (flow meter, generator, submersible pump, water depth meter, stopewatch and a legend for noting the time and other parameters). Pump test for determination of discharge of well and taking sample of water for quality test after water cleaning Under supervission of NCA and PRRD representative. اجرای پمپ تست بخاطردریافت پارامتر هایدروجیولوجیکی (دیسچارج، سطح ستاتیکی آب، سطح دینامیکی، ستون آب درچاه و احیائی مجدد سطح آب) چاه وهمچنان نمونه گیری آب بعد از صاف شدن مکمل برای تعین کیفیت آن تحت نظارت نماینده ریاست احیاء وانکشاف دهات. . | Job | 8 |  | 0
7 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe Diameter: 63 mm inside diameter,16 bar Best quality.پایپ پولی ایتیلین بقطر داخلی 63 ملی با فشارقابل برداشت 16 بار | m | 65 |  | 0
Sub-Total Cost for New Bore well (AFN) |  |  |  |  | 0
BoQ for Solar pump system and transmission line from pump to Elevated Water Tank
1 | Submersible pump (made in italy- padrollow company) with 3 KW- power and Total 56 m head dynamic head (, (4SR8/17) with supply and installation Avg. water production per day: 85m³/day , Total head 56m Invertor+controller High quality with supply and installation accessoreis required پمپ با انورتر که دارائی قطر بدنه 4انچ یا معادل طبق مشخصات داده شده فوق ساخت اروپایی همرای همه وسایل مربوطه | No | 1 |  | 0
2 | Supply and Installation Solar panels 300watt , internationally certified by IEC, ISO, TUV and CE, Range of ambient temperature: 233 .. 358 K Temperature coefficient (Voc): -0.39% /Cº. (Isc): +0.049% /Cº. Weight: 21.5Kg Operating Temperature Range: -40Cº/85Cº, Power tolerance: +3 to 5 % Maximum power voltage: 37.2V Open circuit voltage: 46.2V Max power point current: 8.87 - 9.24A Module shortcut current: 9 - 10 A Minimum power output: 300-330 W Solar module type: POLYCRYSTALLINE or MONOCRYSTALLINE Water proof PV junction boxes IP68 for each array including DC Fuses, DC switch disconnectors, bus bars ,terminals, ducts or trays, supports & labels suitable to the PV arrays loads. 12-years Limited Product Warranty,25-years Limited Performance Warranty. | No | 18 |  | 0
3 | Well probe sensor | set | 1 |  | 0
4 | Cable splice kit 2.5-4mm2 | set | 1 |  | 0
5 | Submercible drop cable (4*10)mm2 from Inverter to submersible water pump کیبل برق از انورتر الی پمپ | m | 80 |  | 0
6 | Power Cable 1*10mm² from Solar panels to Inverter | m | 30 |  | 0
7 | Conduct pipe | m | 80 |  | 0
8 | Power drop cable - 2x1.5mm² for dry running protection | m | 80 |  | 0
9 | Installation of solar pump set and solar panels Ground rod with copper Cable for all system (Solar Panels and pump) Installation of complete set of electrical system (solar panel, submersible pump, inverter) with complete requierment and system check, including supply and installation of Safty rope from plastic for holding of solar water pump, and grounding system including all electrical equipement like (control box, fuse box, and others). سیستم آرتنگ برای سولر پنیل ها و پمپ نصب | set | 1 |  | 0
10 | Supply and installation of Polyethylene 90° bend, Size (63)mm زانوخم 90 درجه نوع پولی ایتیلین | No | 1 |  | 0
11 | Supply and installation of bronze Gate valve (best quality) Nominal Diameter = 2" گیت وال به قطر دو انچ | No | 1 |  | 0
12 | Supply and installation of Galvanized Iron Paddle flange diameter 63 mm(clip on the top of the well to hold up the riser main pipe) کلیپ برای محکم نمودن پایپ و واتر پمپ چاه | No | 1 |  | 0
13 | Supply and installation of Galvanized Iron Nipple, diameter 2" اشتت آهني ملمع جست بقطر | No | 2 |  | 0
14 | Supply and installation of Galvanized Iron Union, diameter 2"پیوند آهني ملمع جست بقطر | No | 1 |  | 0
15 | Supply and installaiton of Female threaded Adopter (FTA), Size (63x2") ادپتر ماده بقطر | No | 2 |  | 0
16 | Supply and installation of bronze non return valve Dia = 2" (best quality) for riser main pipe in pump house, with all related fittings تمبه والو به قطر دو انچ | No | 1 |  | 0
Sub-Total Cost for Solar panels and Submersible pump(AFN) |  |  |  |  | 0
BoQ for Boundary wall of solar panels
1 | کندن کاری درزمین قسم4-3 Excavation for boundary wall and solar pole different ground type | m3 | 100 |  | 0
2 | Stone masonry with cement- sand mortar M:1:5 سنگکاری با مصاله سمنت وریگ مارک مخلوط | m3 | 56 |  | 0
3 | Plain Cement Concrete as per Drawing for Capping and leveling (PCC), M200 kg/cm2 کانکریت بدون سیخ با مارک مخلوطی | m3 | 12 |  | 0
4 | Kilned brick masonry with mortar 1:4 (cement - sand) . خشت کاری پخته به مخلوط مساله 1:4 (ریگ : سمنت) | m3 | 29 |  | 0
5 | Plaster work with cement-sand out and in side the boundry wall M:1:5 پلسترکاری با مخلوط سمنت وریگ مارک مخلوط مصاله | m2 | 200 |  | 0
6 | Painting Wheather Sheet رنگمالی با رنگ معه دو قلم | m2 | 200 |  | 0
| Construciton of Guard room in the ground floor of the reservoir with plastering, Mettalic door and other associated works | LS | 1 |  | 0
7 | Supply and installation of metallic gate by 20 Gauge Russian GI iron sheet with all requirements (complete) according .دروازه آهنی برای احاطه سولر پنیل ها که ضخامت تخته آن 20 گیج روسی باشد معه یم قلم صد زنگ و دو قلم رنگ روغنی با کیفیت عالی تهت نطر انجینر مراقبت کننده با امورات ایجابی | m2 | 2.8 |  | 0
8 | Supply and installation of Concertina wire on boundary wall of solar panel (complete) according to the drawing تهیه ونصب سیم خار در بالائی دیوار احاطه مطابق نقشه | m | 50 |  | 0
Sub-Total Cost for Boundary wall of solar panels (AFN.) |  |  |  |  | 0
BoQ for Solar Panel frame
1 | کندن کاری درزمین قسم4-3 Excavation for boundary wall and solar pole different ground type | m3 | 10 |  | 0
2 | Stone bolder Pitching: Supply and pitching of stone in foundation and surrounding area of well protection box. | m3 | 1 |  | 0
3 | Reinforced Cement Concrete (RCC), including steel bars and shuttering according to the drawings.کانکریت سیخدار با مارک مخلوطی 1.1.5.3 همرای قالب بندی | m3 | 3 |  | 0
4 | Plaster work with cement-sand M: 1:3 for exterioir pillar .M: 1:3. پلسترکاری بیرونی | m2 | 20 |  | 0
5 | Solar Frame: Supply and istallation ( Box Steel (100x50)mm, 2mm thickness Russina or equivalent best quality, Box Section Steel (40x40) mm, 2mm thickness Russian or equivalent best quality, Steel plate (250x25)mm, 8mm thickness russian or equivalent, J- bolt) steel forame size is in the drawing for 18 solar panels (330 watts) and with all other requirements as per desing and insturction of NCA Engineer | Ls | 1 |  | 0
6 | Preparation and smoothing of the gravel for the inner courtyard surrounds soler panels with a thickness of 7 cm. تهیه و هموار کاری جغل برای صحن داخلی احاطه سولر پنل ها به ضخامت 7 سانتی متر | m3 | 10 |  | 0
Sub-Total Cost for solar panels Frame (AFN.) |  |  |  |  | 0
BoQ for 40 m3 (40000 lit) RCC Elevated water Reservoir
1 | Excavation for reservoir in ground type4-5 کندن کاری درزمین قسم | M3 | 70 |  | 0
2 | Stone bolder Pitching: Supply and pitching of stone in foundation and surrounding area of elevated water tank foundation. | M3 | 10.5 |  | 0
3 | Plain Cement Concrete (PCC), M200. کانکریت بیدون سیخ با مارک مخلوطی | M3 | 19 |  | 0
4 | Reinforced Cement Concrete (RCC), M 250kg/cm2 including steel bars and shuttering according to the drawings.کانکریت سیخدار با مارک مخلوطی M250 همرای قالب بندی | M3 | 83 |  | 0
5 | Plaster work with cement-sand (Isomat Product) M: 1:3 for inside. M: 1:3 Plaster work with cement-sand + padlow powder M: 1:3 for inside. Plaster work should be plumb and stright (with wedge profile almunium level screed or چوب ګز), sand should be clean from any unwanted materials (soil, gross plastic etc). . پلسترکاری داخلی با پودر ضد نفوذ آب | M2 | 100 |  | 0
6 | Plaster work with cement-sand M: 1:3 for exterioir wall.M: 1:3. پلسترکاری بیرونی | M2 | 250 |  | 0
7 | Painting Wheather Sheet 100%رنگمالی با رنگ | m2 | 250 |  | 0
8 | Supply and installation of isogam insulation on roof of reservoir. ایزوگام برای پوشش ذخیره | m2 | 30 |  | 0
9 | Supply and installation of iron gate for reservoir manhole and top of reservoir opening (iron with thickness 3mm) with all required activities and as per drawing. دروازه آهنی برای منهول ذخیره و دروازه سر ذخیره با ضخامت 3 ملی متر | No | 1 |  | 0
10 | Supply and installation of 2 inch Galvanised Iron Ladder for reservoir with all required activites according to drawings.زینه از پایپ جستی ملمع شده بقطر 2 انج | No | 1 |  | 0
11 | Galvanized Iron pipe for the inlet of purposed net work, Internal dia.3" with flange پايپ آهني ملمع جستی بقطرداخلي سه انچ همراه با فلنج | m | 16 |  | 0
12 | Supply and installation of bronze Gate valve (best quality) Nominal Diameter = 3" for distribution system گیت وال به قطر دو انچ | No | 1 |  | 0
13 | Supply and installation of Flanged Gate valve (Good quality) Nominal Diameter = 63mm for distribution system best quality گیت وال به قطرسه انچ | No | 2 |  | 0
14 | Supply and installation of Galvanized Iron Socket diameter 3" ساکت آهني ملمع جستی بقطر3 انچ | No | 3 |  | 0
15 | Supply and installation of Galvanized Iron Nipple, diameter 3" اشتت آهني ملمع جستی بقطر3 انچ | No | 3 |  | 0
16 | Supply and installation of Galvanized Iron Union, diameter 3" پیوند آهني ملمع جستی بقطر3 انچ | No | 2 |  | 0
17 | Supply and installation of Galvanized Iron Paddle flange diameter 3" (clip on the top of the well to hold up the riser main pipe) کلپ گیرا برای محکم نمودن پایپ در سرچاه | No | 1 |  | 0
18 | Supply and installation of Galvanized Iron Elbow, diameter 3" زانو خم آهني ملمع جستی بقطر دونیم انچ | No | 4 |  | 0
19 | Supply and installation of End cup for the wash out pipe 3" فلق برای پایپ شستشو | No | 1 |  | 0
20 | Supply and installation of water stopper for elevated water tank as per site engineer approval تهیه و نصب واتر استاپر مطابق تایید انجینر ساحوی پروژه برای ذخیره ی اب | m | 30 |  | 0
21 | Supply and installation of gutter 18 gauge acoording to site and quality control engineer تهیه و نصب ناوه با کیفیت گیچ 18 نظر به خواست انجینر مراقبت کننده | LS | 1 |  | 0
22 | Concrete and construction material testing Construction Specification تست کانکریت ومواد ساختمانی | LS | 1 |  | 0
Sub-Total Cost for 40 m3 (40000 lit) RCC Elevated water Reservoir (AFN.) |  |  |  |  | 0
BoQ for Well Protection
1 | excavation for well protection: Excavation of well protection foundation according to Designed drawing and Site conditions. | m3 | 4 |  | 0
2 | Stone bolder Pitching: Supply and pitching of stone in foundation and surrounding area of well protection box. | m3 | 0.5 |  | 0
3 | P.C.C (Plain Cement Concrete) M(1:2:4) including Varnish steel form, the construction materials should be according to attached Specification. | m3 | 0.35 |  | 0
4 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. کانکریت سیخدار با مارک مخلوطی 1:1.5:3 همرای قالب بندی | m3 | 2 |  | 0
5 | Back filling with soil and excavated material .پرکاری خاک معه تپک کاری | m3 | 1 |  | 0
| Sub-Total Cost for well Protection Box (AFN.) |  |  |  | 0
BoQ for Control valve mainhole for distirbution line (Stone Masonry Valve Box)
1 | Preparation/Excavation: Excavation ground type 3-5 for proposed bore well protection mainhole, to clean site from all existent materails the excavated materials should be put 1.5 m away from sides (Rocky Layer, Hard cutting) According to attached technical drawing, technical specification and engineering considerations. | m3 | 2 |  | 0
2 | Stone bolder Pitching:Supply and pitching of stone in foundation and surrounding area of stand post. | m3 | 0.1 |  | 0
3 | Stone Masonry Work M(1:4) :Stones masonry with 35% mortar(M:300, 1:4) | m3 | 1.2 |  | 0
4 | Plastering Work M(1:3) The plaster should be 2-2.5 cm plastering according to technical requirements, with proper curing. | m2 | 2 |  | 0
| Sub-Total Cost for One Main hole |  |  |  | 0
| Grand-Total Cost for Two Main hole |  |  |  | 0
BoQ for RCC Valve box
1 | excavation for valve: box Excavation of valve box foundation according to Designed drawing and Site conditions. | m3 | 4 |  | 0
2 | Stone bolder Pitching: Supply and pitching of stone in foundation and surrounding area of valve box. | m3 | 1 |  | 0
3 | P.C.C (Plain Cement Concrete) M(1:2:4) including Varnish steel form, the construction materials should be according to attached Specification. | m3 | 0.28 |  | 0
4 | Reinforced Cement Concrete (RCC), M 200kg/cm2 including steel bars and shuttering according to the drawings. کانکریت سیخدار با مارک مخلوطی 1:1.5:3 همرای قالب بندی | m3 | 1.9 |  | 0
5 | Back filling of pipe trench by excavated material پرکاری خاک توسط خاک کنده شده | m3 | 1 |  | 0
| Sub-Total Cost for Valve Box Box (AFN.) |  |  |  | 0
BoQ for House connection and 150 Stand tap
1 | Preparation/Excavation: Excavation ground type 3-5 for proposed STP, to clean site from all existent materails the excavated materials should be put 1.5 m away from sides (Rocky Layer, Hard cutting) According to attached technical drawing, technical specification and engineering considerations and Site conditions. | m3 | 70 |  | 0
2 | Stone bolder Pitching: Supply and pitching of stone in foundation and surrounding area of stand post. | m3 | 35.43 |  | 0
3 | PCC (Plain Cement Concrete), M(1:2:4) Mix ratio with all required work and labor cost for base of foundation with 7 days curing and watering of STP , According to attached drawing and site focal point instruction. | m3 | 38 |  | 0
4 | House Connection Fittings: house connection from Main pipe to inside of house with all its features and accessories (PE-FTA, GI-Gate Valve (best Quality), Water Meter(Best Quality) 1/2", Non-Returning Valve 1/2", Water Tap (Best Quality)1/2", PPR-FTA 1/2", PPR Elbow 1/2", PPR-Pipe 16 Bars 1/2",HDPE pipe 1/2" from main pipe to tap, PVC pipe and Water Meter Box (Best Quality, Heavy duty) with prefabricated heavy duty two jet water meter Box including all concerte painitng, and plaster works with any other requiremensts and works. | Ls | 1 |  | 0
Sub-Total Cost for BoQ for 150 Nos Stand Tabs (AFN.) |  |  |  |  | 0
BoQ for Distribution line (From Water tank to House Connection )
1 | Excavation of pipe trench for distribution pipes laying in ground (Soft Soil, Hard Cutting) ) typeکندن کاری درزمین قسم 5-3 | m3 | 3000 |  | 0
2 | Bedding and backfill sand or sieved soil around pipes.پرکاری با ریګ یا خاک غربال شده | m3 | 1000 |  | 0
3 | Supply and installation of Caution tap in pipe trench نوار خطر | m | 1475 |  | 0
4 | Back filling of pipe trench by excavated material.پرکاری خاک معه تپک کاری | m3 | 1500 |  | 0
5 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 16 SDR 11), Outside Diameter: 25 mm, wall thickness (2.3-2.7)mm ,weight 0.173 kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. پایپ پولی ایتیلین بقطر خارجی 25 ملی با فشار قابل برداشت 16 بار | m | 740 |  | 0
6 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 40 mm, wall thickness (2.4-2.8)mm ,weight 0.29kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. پایپ پولی ایتیلین بقطر خارجی 40 ملی با فشار قابل برداشت 10 بار | m | 3253 |  | 0
7 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 50 mm, wall thickness (3-3.4)mm ,weight 0.45kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. پایپ پولی ایتیلین بقطر خارجی 50 ملی با فشار قابل برداشت 10 بار | m | 907 |  | 0
8 | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 10 SDR 17), Outside Diameter: 63 mm, wall thickness (3.8-4.3) mm ,weight 0.72kg/m, Conforming To ISO 4427, DIN 8074-8075 & PrEN 12201 Spesifications. پایپ پولی ایتیلین بقطر خارجی 63 میلی با فشار قابل برداشت 10 بار | m | 568 |  | 0
9 | Supply and installation of bronze Gate valve (best quality) Nominal Diameter = 40mm گیت وال به قطر 40 ملی متر | No | 1 |  | 0
10 | Supply and installation of bronze Gate valve (best quality) Nominal Diameter = 50mm گیت وال به قطر 50 ملی متر | No | 2 |  | 0
11 | PE Fittings 16-10 Bars with plumbing works: Supply, Installation, Laying and fitting of HDPE+GI pipes (Flanged adapter, Sockets, Elbows, TEEs, Saddle Clamps, Reducers, M/F Adapter, Gate valve and etc.) with Supplying and installation according to drawing and its specifications | No | 1 |  | 0
12 | Supply and installation of additional fittings as required | LS | 1 |  | 0
Sub-Total Cost for distribution line (USD.) |  |  |  |  | 0
1 | Sign Board for project لوحه برای پروژه | No | 1 |  | 0
| Grand Total Cost (AFN.) قیمت مجموعی به |  |  |  | 0 | 0
| Prepared by: Eng. Zar Mohammad Ahmadzai |  |  | Checked by: Eng. Farhad Aaqeb