## BoQ
Rural Rehabilitation Association for Afghanistan (RRAA)
East Region Office (ERO)
Province: Nangarhar |  |  |  | DRA – Afghanistan Joint Response 2024-2026
District:Bati kot |  |  |  | Engineering Department
Village: Surobi Ghaziabad |  |  |  | Bill Of Quantity (BoQ) 25 M3 Elevated RCC Water Tank
Project : | RCC water tank V = 25 m3
Date: 11 /08/2024
Bold items to be filled in by tendered (A1,A2. . Etc.). Light items are for cost estimation purposes only
Title | No. | Norm/ unit | A* | Item | Quantity | Unit | Unit cost | Total cost | Remarks
|  |  | Norm |  |  |  | Afs | Afs
A1 | 1 |  |  | Site preparation | 150 | m2
| 1.01 | 0.2 |  | Site preparation, clearing site ect. | 30 | md
Preparation of site for the project, preparation of hand tools and equipment
A2 | 2 |  |  | Excavation for Elevated RCC Water Tank ,valve box ,Solar Panel stand &boundary wall | 70 | m3
| 2.01 | 1 | 1 | Unskilled labour | 70 | md
Excavation of foundation in grad 3- 4 land
A3 | 3 |  |  | Shuttering for Elevated RCC Water Tank and boundary wall | 298 | m2
| 3.01 | 0.02 |  | Wooden timber | 5.96 | m3
| 3.02 | 2 |  | Wooden pole 4m long | 350 | pcs
| 3.03 | 0.05 |  | Nail | 14.9 | kg
| 3.04 | 0.05 |  | Skilled labour on site | 14.9 | md
| 3.05 | 0.07 |  | Unskilled labour on site | 20.86 | md
the shuttering will be well tied, and not use the plank mor than 3 times
A4 | 4 |  |  | PCC (under stone, floor, valve box,stand tap,room,stand )M:150,1:2:4 | 55.6 | m3
| 4.01 | 0.386 |  | Sand | 21.4616 | m3
| 4.02 | 0.771 |  | Gravel | 42.8676 | m3
| 4.03 | 230 |  | Cement | 12788 | kg
| 4.04 | 115 |  | water | 6394 | liter
| 4.05 | 0.65 |  | Skilled labor on site | 36.14 | md
| 4.06 | 1.35 |  | Unskilled labour on site | 75.06 | md
A5 | 5 |  |  | Stone Masonry of boundary wall ,room,Gate valve box & Res with 35% mortar (M300, 1:4) | 53.76 | m3
| 5.01 | 1 |  | Stone with transportation | 53.76 | m3
| 5.02 | 0.394 |  | Sand | 21.1814 | m3
| 5.03 | 95 |  | Cement | 5107.2 | kg
| 5.04 | 48 |  | water | 2580.48 | liter
| 5.05 | 0.5 |  | Skilled labour on site | 26.88 | md
| 5.06 | 1 |  | Unskilled labour on site | 53.76 | md
A6 | 6 |  |  | Pointing with mortar (M300, 1:4) | 53 | m2
| 6.02 | 0.054 |  | Sand | 2.862 | m3
| 6.03 | 2.2 |  | Cement | 116.6 | kg
| 6.04 | 1 |  | water | 53 | liter
| 6.05 | 0.17 |  | Skilled labour on site | 9.01 | md
| 6.06 | 0.05 |  | Unskilled labour on site | 2.65 | md
A7 | 7 |  |  | Bricks masonry with burned bricks with 25% mortar(M:300, 1:4) | 29.6 | m3
| 7.01 | 520 |  | Brick including transportation(Size, 22*11*7cm ) | 15392 | pcs
| 7.02 | 0.27 |  | Sand | 7.992 | m3
| 7.03 | 80 |  | Cement | 2368 | kg
| 7.04 | 40 |  | water | 1184 | liter
| 7.05 | 0.65 |  | Skilled labour on site | 19.24 | md
| 7.06 | 1.8 |  | Unskilled labour on site | 53.28 | md
A8 | 8 |  |  | Steel working (footing+column+slab ) | 5888 | kg
| 8.02 |  |  | Steel bar 8 mm Khan Steel | 568.94 | kg
| 8.03 |  |  | Steel bar 10 mm Khan Steel | 355 | Kg
| 8.04 |  |  | Steel bar 12 mm Khan Steel | 1410 | Kg
| 8.05 |  |  | Steel bar 14 mm Khan Steel | 870 | Kg
| 8.06 |  |  | Steel bar 16 mm Khan Steel | 1040 | Kg
| 8.07 |  |  | Steel bar 18 mm Khan Steel | 714 | Kg
| 8.08 |  |  | Steel bar 20 mm Khan Steel | 930 | Kg
| 8.09 |  |  | Wire 1 mm | 28 | Kg
| 8.1 | 0.01 |  | Skilled labour on site | 58.88 | md
| 8.11 | 0.009 |  | Unskilled labour on site | 52.992 | md
the steel should be without rust, the tensile stress of steel is 2400 kg/cm2, and for deformed bars is 2800 kg/cm2 for the trust refer to the design and specification
A9 | 9 |  |  | RCC (footing+column+slab ) of Elevated Water reservoir, Gate valve and Guard room ( M:250,1:1:2) | 62 | m3
| 9.01 | 0.338 |  | Sand | 20.956
| 9.02 | 0.676 |  | Gravel | 41.912 | m3
| 9.03 | 400 |  | Cement | 24800 | kg
| 9.04 | 200 |  | water | 12400 | liter
| 9.05 | 0.7 |  | Skilled labour on site | 43.4 | md
| 9.06 | 2 |  | Unskilled labour on site | 124 | md
| 9.07 |  |  | water for curing
A10 | 10 |  |  | Door and Windows for Guard room and bathroom( PVC) | 6.85 | m2
| 10.01 |  |  | I- beam (steel girder) 100mmX100mm, 5mm thick, 280cm long | 2.2 | M
| 10.02 |  |  | T-iron galvanized steel 4mm thick & 370cm long | 18 | M
| 10.01 |  |  | Bitumen cover for preventing leakage (ezogam) | 40 | m2
| 10.02 | 0.33 |  | PVC door (1mX2m)(0.8mX1.8m) | 2 | pcs
| 10.03 | 1 |  | PVC window (1.5mX1.5m) (0.4mX0.4m) | 2 | pcs
| 10.04 |  |  | First class burnt brick (chowka) | 60 | pcs
| 10.05 | 0.1 |  | Skilled labour on site | 2 | md
| 10.06 | 0.1 |  | Unskilled labour on site | 2 | md
A11 | 11 |  |  | Plastering of reservoir, boundary wall ,stand tap & guard room with cement mortar (M:300,1:4) | 458 | m2
| 11.01 | 0.025 |  | Sand | 11.45 | m3
| 11.02 | 6 |  | Cement | 2748 | kg
| 11.03 | 8 |  | water | 3664 | liter
| 11.04 | 0.1 |  | Skilled labour on site | 45.8 | md
| 11.05 | 0.1 |  | Unskilled labour on site | 45.8 | md
A12 | 12 |  |  | Plastering 1:3 (chips) with padllow powder inside of reservoir | 12 | m2
| 12.01 | 0.022 |  | Sand | 0.264 | m3
| 12.02 | 8.8 |  | Cement | 105.6 | kg
| 12.03 | 0.08 |  | padllow powder | 0.96 | kg
| 12.04 | 0.1 |  | Skilled labor on site | 1.2 | md
| 12.05 | 0.2 |  | Unskilled labor on site | 2.4 | md
A13 | 13 |  |  | Filling with gravel 15 cm of floor and compaction for solar stand and guard room | 20 | m3
| 13.01 | 1 |  | Local stone | 20 | m3
| 13.02 | 0.3 |  | Unskilled labour | 6 | md
The soil will be well compacted
A14 | 14 |  |  | Oil painting for Hand Role,door and Stairs | 24 | m2
| 14.01 | 0.5 |  | Plastic Paint 50% inside | 12 | kg
| 14.02 | 0.03 |  | white glue | 0.72 | kg
| 14.03 | 0.5 |  | Marble powder | 12 | kg
| 14.04 | 0.05 |  | Powder glue | 1.2 | kg
| 14.05 | 0.22 |  | Oil paint | 5.28 | kg
| 14.06 | 0.25 |  | Skilled labour | 1.32 | md
Two layer plastic painting on walls, Two layer plane painting of out side, 3 layer of oil painting.
A15 | 15 |  |  | White washing inside with 30% emulsion | 458 | m2
| 15.01 | 0.5 |  | Plastic Paint 30% inside | 229 | kg
| 15.02 | 0.03 |  | Skilled labour | 13.74 | md
| 15.03 | 0.04 |  | Unskilled labour on site | 18.32 | md
Inside the rooms two layer plastic, outside the block two layer plane and door and windows oil painting 3 layers.
A16 | 16 |  |  | Electrical work | 25 | m
| 16.01 |  |  | Main Switch | 1 | pcs
| 16.02 |  |  | Switch for Bulb | 2 | pcs
| 16.03 |  |  | Storage battery 100 amp made in thailand | 1 | pcs
| 16.04 |  |  | Solar panel 250 watt made in china (with stand) | 1 | pcs
| 16.05 |  |  | Solar fane | 1 | pcs
| 16.06 |  |  | Guard room Carpet | 16 | m2
| 16.07 |  |  | Saket under plaster | 2 | pcs
| 16.08 |  |  | Electric cable (4X6) | 15 | m
| 16.09 |  |  | Wire (2x2.5) | 10 | m
| 16.1 | 0.12 |  | Electrician | 3 | md
All the electrical material will be Iranian or Garman made.
A17 | 17 |  |  | Hand Role and Stairs | 1 | Lum Sum
| 17.01 |  |  | Supply and installation of 2 inch Iron Ladder for reservoir with all required activites according to drawings. | 25 | m
| 17.02 |  |  | Supply and installation of 1.5 inch Galvanised Iron Ladder for inter reservoir with all required activites according to drawings. | 5 | m
| 17.03 |  |  | Steel Plate ( 32 x 4 ) mm L= 2.7 No.6 (safety ) | 18 | m
| 17.04 |  |  | Steel pipe 1 inch diameter L= 6.5m) No.4 for tank | 25 | m
| 17.05 |  |  | Steel pipe 0.5 inch diameter L= 0.5 m) no.8 for tank | 4 | m
| 17.06 |  |  | Steel bar 20 mm dia l= 1.5 m no. 4 for tank | 6 | m
| 17.07 |  |  | Angle iron ( 50 x 50 x 4 ) mm L= 1 m) No.4 | 4 | m
| 17.08 |  |  | GI pipe 1.5 inch diameter ( hand role) L= 6.5 m) No.4 | 26 | m
| 17.09 |  |  | Steel pipe 1 inch diameter ( hand role) L= 6.5 m) No.4 | 26 | m
| 17.1 |  |  | Steel pipe 1 inch diameter ( hand role)L= 1 m) No.46 | 46 | m
| 17.11 |  | 0.2 | Skilled labour on site | 3 | md
| 17.12 |  | 0.075 | Unskilled labour on site | 6 | md
A18 | 18 |  |  | GI & PE pipe Fittings ( water supply system) | 2478 | m
| 18.01 |  |  | GI Pipe 2 1/2 inch( 63mm) ( inflow pipe ), thickness 2 - 3mm ,best quality | 18 | m
| 18.02 |  |  | GI Pipe 2 1/2 inch ( 63mm)( outflow pipe ) thickness 2 - 3mm best quality | 6 | m
| 18.03 |  |  | GI Pipe 2 1/2inch (63mm)( Supply pipe ) thickness 2 - 3mm with flange, best quality | 18 | m
| 18.04 |  |  | GI Pipe 3 inch 75mm)( drainage or cleaning pipe ) thickness 2 - 3mm, best quality | 3 | m
| 18.05 |  |  | Air vent pipe 2 inch (50mm)=1m | 1 | pcs
| 18.08 |  |  | Coupling 2 inch (50mm) diameter, best quality | 6 | pcs
| 18.09 |  |  | Coupling 3 inch (75mm) diameter, best quality | 4 | pcs
| 18.1 |  |  | GI Joint 2 (50mm) and 2 1/2 inch ( 63mm) diameter,best quality | 8
| 18.11 |  |  | Joint 1,1.5,2.5 (25,40,50,63)mm and 2 inch diameter, best quality | 13 | pcs
| 18.12 |  |  | Nipple 2 inch (50mm) diameter, best quality | 4 | pcs
| 18.13 |  |  | Nipple 2.5 inch (63mm)diameter, best quality | 4 | pcs
| 18.14 |  |  | Elbow 0.5 inch (12.5mm) diameter, best quality | 68 | pcs
| 18.15 |  |  | Elbow 2.5 inch (63mm)diameter, quality | 5 | pcs
| 18.16 |  |  | Glass wool insulation 2 layers t= 67.5 cm | 30 | m2
| 18.17 |  |  | PE Tee (T) 0.5 inch (12.5mm)diameter, best quality | 30 | pcs
| 18.18 |  |  | PE Tee (T)1 1/2inch (40mm)diameter, best quality | 25 | pcs
| 18.19 |  |  | PE Tee (T) 2 inch(50mm) diameter, best quality | 20 | pcs
| 18.2 |  |  | PE Tee (T) 2 1/2 inch (63mm)diameter, best quality | 15 | pcs
| 18.21 |  |  | PE pipe 1.5 inch (40mm) for water supply (PE 100, PN10, SDR 17) 10 bar weight 0.297 kg/m, best quality | 309 | m
| 18.22 |  |  | PE pipe 3 inch (75mm) for water supply (PE 100, PN10, SDR 17) 10 bar weight 1.02 kg/m, best quality | 220 | m
| 18.23 |  |  | PE pipe 2.5 inch ( 63mm) for water supply (PE 100, PN10, SDR 17) 10 bar weight 0721 kg/m, best quality | 357 | m
| 18.24 |  |  | PE pipe 2 inch (50mm) for water supply (PE 100, PN10, SDR 17) 10 bar weight 0.453 kg/m, best quality | 823 | m
| 18.25 |  |  | PE pipe 1 1/4inch (32mm) (PE 100, PN10, SDR 17) 10 bar weight 0.187 kg/m, quality | 248 | m
| 18.26 |  |  | PE pipe 1 inch (25mm) (PE 100, PN10, SDR 17) 10 bar weight 0.137 kg/m, quality | 504 | m
| 18.27 |  |  | PE pipe 3.5 inch (90mm)for water supply (PE 100, PN10, SDR 17) 10 bar weight 1.46 kg/m, best quality | 17 | m
| 18.28 |  |  | Gate valve 1.5" best quality | 6 | pcs
| 18.29 |  |  | Gate valve 2.5" best quality | 1 | pcs
| 18.3 |  |  | Gate valve 2" best quality | 1 | pcs
| 18.31 |  |  | Check valve 2" best quality | 3 | pcs
| 18.32 |  |  | Gate valve 2.5" for reservoir best quality | 2 | pcs
| 18.33 |  |  | Socket 3 inch(75mm)dia best quality | 3 | pcs
| 18.34 |  |  | Socket 2 inch (50mm)dia best quality | 15 | pcs
| 18.35 |  |  | Socket 1 inch (25mm) dia best quality | 15 | pcs
| 18.36 |  |  | Reducer 0.5 x3/4' (12.5*19)mm best quality | 1 | pcs
| 18.37 |  |  | Niple 0.5" = 12.5mm best quality | 68 | pcs
| 18.38 |  |  | PE female adapter 20X0.5" best quality | 45 | pcs
| 18.39 |  |  | Glass wool 2cm thick w=10, L=2m | 20 | m2
| 18.4 |  |  | GI pipe 0.5 inch thickness 2 - 3mm, best quality | 68 | m
| 18.41 |  |  | Top 0.5 Zahid best quality | 45 | pcs
| 18.42 |  |  | End cap, 40mm best quality | 8 | pcs
| 18.43 |  |  | End cap, 50mm best quality | 6 | pcs
| 18.44 |  |  | End cap, 630mm best quality | 4 | pcs
| 18.45 |  |  | End cap,75mm best quality | 2 | pcs
| 18.46 |  |  | Measurement meter for water , best quality | 45 | pcs
| 18.47 |  |  | Meter box Sedaqat Mohmand 4.2kg best quality | 45 | pcs
| 18.48 |  |  | Supply and installation of water stopper for joint between floor slab and walls insulation (225 mm width, 15mm thick) | 13.2 | M
| 18.49 |  |  | Supply and installation of best quality well probe sensor, for protection of submersible water pump with complete set | 1 | set
| 18.5 |  |  | Power Cable 2*1.5mm2 for sensor. (best quality) | 95 | M
| 18.51 |  | 0.25 | Plumber | 15 | md
| 18.52 |  | 0.25 | Unskilled labour on site | 15 | md
A19 | 19 |  |  | Water pump and Solar panels with stand (with guarantee) | 1 | Lum Sum
| 19.01 |  |  | Supply, transportation of Submersible pump with its Compatible inverter, control box and Fuse box in stainless steel. EN 1.4301 (AISI 304).EN 1.4301 (AISI 304). EN 1.4539 (AISI 904L). Rated power P2 = 3 kW, Rated voltage: 3 x 220-230 V Compatible inverter: 4 KW, IP65-68, Pure sine wave, VFD and soft starter Avg. water production per day: (9.43 m³/h) 75 m³/day, Total dynamic head: 50m , Pump Max head:100m Solar pump 3 KW according to the technical specification and requirement, Contractor must submit manufacturer warranty for solar Pump for a period not less than 2 years. Contractor must submit all the required certificates for solar pump Serial number of Solar pump should be certified by manufacturing company, Supply and transportation of solar pump set | 1 | No |  |  | ظرفیت آب دهی پمپ = 9.43m3/hour باشد و در صورت پایین آمدن سطح آب پمپ بشکل اتوماتیک خاموش شود
| 19.02 |  |  | Supply and transportation of Solar panels 5000 watt internationaly certified by IEC, ISO, TUV and CE Range of ambient temperature: 233 .. 358 K Temperature coefficient (Voc): -0.31% /Cº Power tolerance: +3 to 5 % Maximum power voltage: 32 - 33.2V Open circuit voltage: 38 - 39.5V Max power point current: 8.5 - 9.5A Module shortcut current: 9 - 10 A Minimum power output: 5000 W Solar module type: POLYCRYSTALLINE Water proof PV junction boxes IP68 for each array including DC Fuses, DC switch disconnectors, bus bars ,terminals, ducts or trays, supports & labels suitable to the PV arrays loads. Contractor must submit manufacturer warranty for solar panel for a period not less than 25 years. Contractor must submit all the required certificates for each PV solar panel from Serial number of PV Panel should be certified by manufacturing company Supply and transportation of solar pump set and solar panels | 5000 | Watt |  |  | سولر ساخت کشور جرمنی ویا 11 شرکت ثبت شده در وزارت انکشاف دهات بوده و در هر نوع آب و هوا سازگار بوده و بشترین بازدهی را دارا باشند
| 19.03 |  |  | Fixed steel frame (stand) for Solar panels, with the adjustable tilt angle between 35 to 45 degree, for more details refer to drawing | 1 | No
| 19.04 |  |  | Supply and installtion of metal box for Inverter and other Switches (best quality) | 1 | set
| 19.05 |  |  | Best quality Submersible Drop Cable (4*4)mm² from Inverter to Submersible water pump with clips, nails and complete installation | 250 | M
| 19.06 |  |  | Submersible Drop Cable 4*4mm² from Inverter to Submersible water pump | 250 | M
| 19.07 |  |  | Best quality Power cable (2*6)mm2 for solar panels connection and from solar panels to inverter icluding connectors, tape, plastic conduits and complete installation. | 100 | M
| 19.08 |  |  | Power Cable 2*1.5mm² for float switch ( Level switch from inverter to water tank) | 25 | M
| 19.09 |  |  | Power Cable 2*1.5mm2 for float switch (Level switch from inverter to water tank) with installation and clips. (best quality) | 250 | M
| 19.1 |  |  | Installation of complete set of electrical system (solar panel, submersible pump, inverter) with complete requierment and system check, with Safty rope, plastic for holding of solar water pump | 1 | JOB
| 19.11 |  |  | Supplying, installation, laying and fitting in place of High Density Polyethylene pipe (PE 100 PN 12.5 SDR 13.6), Outside Diameter: 50 mm, wall thickness ( 3.7- 4.2) mm, weight 0.55 kg/m, Conforming To ISO 4427,DIN8074&PrEN12201 Spesifications. | 80 | M
| 19.12 |  |  | Grounding Rod with Copper Cable | 1 | set
A20 | 20 |  |  | Security wires above boundary wall | 51 | m
| 20.01 |  |  | Metal tube 50mm dia | 18 | m
| 20.02 |  |  | Angle iron (3cmX3cm) 3mm thick | 51 | m
| 20.03 |  |  | Concertina string (60cm circle dia) | 180 | m
| 20.04 |  |  | Galvanized wire for concertina fixation | 270 | m
| 20.05 |  | 0.085 | Skilled labour on site | 4.335 | md
| 20.06 |  | 0.172 | Unskilled labour on site | 8.772 | md
A21 | 21 |  |  | Main Gate for boundary wall | 1 | pcs
| 21.01 |  |  | Main gate (Centenary 1.50mX1.40m) | 1 | pcs
A22 | 22 |  |  | Digging of bore well | 1 | Lum Sum
| 22.01 |  |  | Well drilling according to the type of earth layers with (cobai machine, diameter (16") depends on soil texture and taking sample of each Geological formation. | 80 | m
| 22.01 |  |  | Supply and Installation of PVC casing pipe class -D, dia.8" Super Royal PVC pipe D Class10.5kg/m | 50 | M
| 22.01 |  |  | Supply and installation of Filter pipe PVC Class-D. 8 inch dia. Total area for filter pipe openings should not be more than 25% of total area. Super Royal PVC pipe D Class10.5kg/m and AND CAP 8" | 30 | M
| 22.02 |  |  | Saftey rope Ø10mm for holding of solar pump | 100 | M
| 22.03 |  |  | Gravel Packing from sorted gravel round washed gravel the size of gravel should be determind after well drilling accordding to the sample of starta. | 8 | M3
| 22.04 |  |  | Back filling for casing pipe should be clay soil without gravel stone | 4 | m3
| 22.05 |  |  | Complete Water test( Complete physical, chemical and bacteriological tes) | 1 | no
| 22.06 |  |  | Well and Network chlorination before used the drinking Water | 1 | no
| 22.07 |  |  | Pump Test for the 8 hours with document . Cleaning and compressor Work | 1 | no
A23 | 23 |  |  | Excavation & backfilling for Pipe Network(Excavation of pipe Network in grad 3-4 land | 848 | m3
| 23.01 |  |  | Sand filling under and above water supply pipe | 230 | m3
| 23.02 |  | 0.6 | Unskilled labour | 424 | md
A24 | 24 |  |  | Site tools & Moblization | 1 | Lum Sum
24.01
| 24.01 |  |  | technical survey by third Parti in the RFQ (20000)AFN | 1 | Lum Sum
| 24.02 |  |  | Salary for one foreman for implementation and arrangement of project work introduced by RRAA during implementation process.in the RFQ (60000)AFN | 3 | Months
| 24.03 |  |  | Safety kit for labour (the site of pipe Scheme ) | 40 | pcs
| 24.04 |  |  | Kit for maintenance specified in the RFQ (20000)AFN | 20 | pcs
| 24.05 |  |  | Signboard for pipe scheme (40*60)cm | 1 | pcs
| 24.06 |  |  | Logos and Massages | 1 | Lum Sum
| 24.07 |  |  | Vase for the Pipe Scheme site | 40 | pcs
| 24.08 |  |  | Mobilization on site Pipe Scheme site | 1 | Lum Sum
24.09
Total cost of activities (A1+A2+……..+A24)
2% government tax inlcuded | [7 empty] | 0
Note: the transportation cost of materials and equipments of items should include to unit cost of each activities.